## AlarmList
Sheet type | Alarm list | Alarm list
|  | Alarm type | Alarm tag | Signal tag | Delay(ms) | Limit type | Priority | Ack. Required | Digital alarm |  | Analog alarm |  | Description
[9 empty] | Inverted | Bit no. | Limit | Hysteresis
|  | Digital | Genset1.Engine.OverloadAlarm | Genset1.Engine.Overload |  | HighHigh | Priority1 | FALSE |  |  |  |  | Genset1 engine overload
|  | Digital | Genset1.Engine.LoadWarning | Genset1.Engine.HighLoad |  | High | Priority2 | FALSE |  |  |  |  | Genset1 engine high load warning
|  | Digital | Genset2.Engine.OverloadAlarm | Genset2.Engine.Overload |  | HighHigh | Priority1 | FALSE |  |  |  |  | Genset2 engine overload
|  | Digital | Genset2.Engine.LoadWarning | Genset2.Engine.HighLoad |  | High | Priority2 | FALSE |  |  |  |  | Genset2 engine high load warning
|  | Digital | Hybrid.Battery.CellTemperatureDiffWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 0 |  |  | Cell temperature difference warning
|  | Digital | Hybrid.Battery.CellVoltageDiffWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 1 |  |  | Cell voltage difference warning
|  | Digital | Hybrid.Battery.TemperatureOverflowChargeWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 2 |  |  | Temperature overflow charge warning
|  | Digital | Hybrid.Battery.TemperatureUnderflowChargeWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 3 |  |  | Temperature underflow charge warning
|  | Digital | Hybrid.Battery.TemperatureOverflowDischargeWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 4 |  |  | Temperature overflow discharge warning
|  | Digital | Hybrid.Battery.TemperatureUnderflowDischargeWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 5 |  |  | Temperature underflow discharge warning
|  | Digital | Hybrid.Battery.TotalVoltageOverflowWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 6 |  |  | Total voltage overflow warning
|  | Digital | Hybrid.Battery.TotalVoltageUnderflowWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 7 |  |  | Total voltage underflow warning
|  | Digital | Hybrid.Battery.CellVoltageOverflowWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 8 |  |  | Cell voltage overflow warning
|  | Digital | Hybrid.Battery.CellVoltageUnderflowWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 9 |  |  | Cell voltage underflow warning
|  | Digital | Hybrid.Battery.CellVoltageDifferenceWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 10 |  |  | Cell voltage difference warning
|  | Digital | Hybrid.Battery.StateOfChargeUnderflowWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 11 |  |  | State of charge underflow warning
|  | Digital | Hybrid.Battery.StateOfChargeJumpWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 12 |  |  | State of charge jump warning
|  | Digital | Hybrid.Battery.InsulationLowWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 13 |  |  | Insulation low warning
|  | Digital | Hybrid.Battery.AmbientTemperatureUnderflowWarning | Hybrid.ESS.WarningWord1 |  | Low | Priority2 | FALSE |  | 14 |  |  | Ambient temperature underflow warning
|  | Digital | Hybrid.Battery.AmbientTemperatureOverflowWarning | Hybrid.ESS.WarningWord1 |  | High | Priority2 | FALSE |  | 15 |  |  | Ambient temperature overflow warning
|  | Digital | Hybrid.Battery.CellTemperatureDiffFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 0 |  |  | Cell temperature difference alarm
|  | Digital | Hybrid.Battery.CellVoltageDiffFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 1 |  |  | Cell voltage difference alarm
|  | Digital | Hybrid.Battery.TemperatureOverflowChargeFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 2 |  |  | Temperature overflow charge alarm
|  | Digital | Hybrid.Battery.TemperatureUnderflowChargeFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 3 |  |  | Temperature underflow charge alarm
|  | Digital | Hybrid.Battery.TemperatureOverflowDischargeFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 4 |  |  | Temperature overflow discharge alarm
|  | Digital | Hybrid.Battery.TemperatureUnderflowDischargeFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 5 |  |  | Temperature underflow discharge alarm
|  | Digital | Hybrid.Battery.TotalVoltageOverflowFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 6 |  |  | Total voltage overflow alarm
|  | Digital | Hybrid.Battery.TotalVoltageUnderflowFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 7 |  |  | Total voltage underflow alarm
|  | Digital | Hybrid.Battery.CellVoltageOverflowFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 8 |  |  | Cell voltage overflow alarm
|  | Digital | Hybrid.Battery.CellVoltageUnderflowFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 9 |  |  | Cell voltage underflow alarm
|  | Digital | Hybrid.Battery.CellVoltageDifferenceFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 10 |  |  | Cell voltage difference alarm
|  | Digital | Hybrid.Battery.StateOfChargeUnderflowFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 11 |  |  | State of charge underflow alarm
|  | Digital | Hybrid.Battery.StateOfChargeJumpFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 12 |  |  | State of charge jump alarm
|  | Digital | Hybrid.Battery.InsulationLowFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 13 |  |  | Insulation low alarm
|  | Digital | Hybrid.Battery.AmbientTemperatureUnderflowFault | Hybrid.ESS.FaultWord1 |  | LowLow | Priority1 | FALSE |  | 14 |  |  | Ambient temperature underflow alarm
|  | Digital | Hybrid.Battery.AmbientTemperatureOverflowFault | Hybrid.ESS.FaultWord1 |  | HighHigh | Priority1 | FALSE |  | 15 |  |  | Ambient temperature overflow alarm
|  | Digital | Hybrid.Battery.DischargeCurrentOverflowFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 0 |  |  | Discharge current overflow alarm
|  | Digital | Hybrid.Battery.ChargeCurrentOverflowFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 1 |  |  | Charge current overflow alarm
|  | Digital | Hybrid.Battery.DCDCfault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 2 |  |  | DCDC fault
|  | Digital | Hybrid.Battery.HVILfault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 3 |  |  | HVIL fault
|  | Digital | Hybrid.Battery.AirDraftFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 4 |  |  | Air draft fault
|  | Digital | Hybrid.Battery.PrechargeFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 5 |  |  | Precharge fault
|  | Digital | Hybrid.Battery.TemperatureMeasurementFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 6 |  |  | Temperature measurement fault
|  | Digital | Hybrid.Battery.CellVoltageMeasurementFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 7 |  |  | Cell voltage measurement fault
|  | Digital | Hybrid.Battery.EmergencyStopActivatedBatterySystem | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 8 |  |  | Emergency stop activated battery system
|  | Digital | Hybrid.Battery.ProtectFunctionFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 9 |  |  | Protect function fault
|  | Digital | Hybrid.Battery.HeartbeatFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 10 |  |  | Heartbeat fault
|  | Digital | Hybrid.Battery.EmergencyStop | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 11 |  |  | Emergency stop
|  | Digital | Hybrid.Battery.ESSTimedOutFault | Hybrid.ESS.FaultWord2 |  | HighHigh | Priority1 | FALSE |  | 12 |  |  | ESS timed out due to precharged drive, but grid drive not running
|  | Digital | Hybrid.Battery.DischargeCurrentShutdown | Hybrid.ESS.ShutdownWord2 |  | HighHigh | Priority1 | FALSE |  | 0 |  |  | Discharge current overflow shutdown
|  | Digital | Hybrid.Battery.ChargeCurrentShutdown | Hybrid.ESS.ShutdownWord2 |  | HighHigh | Priority1 | FALSE |  | 1 |  |  | Charge current overflow shutdown
|  | Digital | Hybrid.Battery.CellTemperatureDiffShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 0 |  |  | Cell temperature difference shutdown
|  | Digital | Hybrid.Battery.CellVoltageDiffShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 1 |  |  | Cell voltage difference shutdown
|  | Digital | Hybrid.Battery.TemperatureOverflowChargeShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 2 |  |  | Temperature overflow charge shutdown
|  | Digital | Hybrid.Battery.TemperatureUnderflowChargeShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 3 |  |  | Temperature underflow charge shutdown
|  | Digital | Hybrid.Battery.TemperatureOverflowDischargeShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 4 |  |  | Temperature overflow discharge shutdown
|  | Digital | Hybrid.Battery.TemperatureUnderflowDischargeShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 5 |  |  | Temperature underflow discharge shutdown
|  | Digital | Hybrid.Battery.TotalVoltageOverflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 6 |  |  | Total voltage overflow shutdown
|  | Digital | Hybrid.Battery.TotalVoltageUnderflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 7 |  |  | Total voltage underflow shutdown
|  | Digital | Hybrid.Battery.CellVoltageOverflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 8 |  |  | Cell voltage overflow shutdown
|  | Digital | Hybrid.Battery.CellVoltageUnderflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 9 |  |  | Cell voltage underflow shutdown
|  | Digital | Hybrid.Battery.CellVoltageDifferenceShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 10 |  |  | Cell voltage difference shutdown
|  | Digital | Hybrid.Battery.StateOfChargeUnderflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 11 |  |  | State of charge underflow shutdown
|  | Digital | Hybrid.Battery.StateOfChargeJumpShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 12 |  |  | State of charge jump shutdown
|  | Digital | Hybrid.Battery.InsulationLowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 13 |  |  | Insulation low shutdown
|  | Digital | Hybrid.Battery.AmbientTemperatureUnderflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 14 |  |  | Ambient temperature underflow shutdown
|  | Digital | Hybrid.Battery.AmbientTemperatureOverflowShutdown | Hybrid.ESS.ShutdownWord1 |  | HighHigh | Priority1 | FALSE |  | 15 |  |  | Ambient temperature overflow shutdown
|  | Digital | Hybrid.PMS.ESS_Fault | Hybrid.ESS.StatusFault |  | HighHigh | Priority1 | FALSE |  |  |  |  | ESS fault
|  | Digital | Hybrid.PMS.LowCriticalVoltageIslandMode | Hybrid.ESS.LowCriticalVoltageIslandMode |  | LowLow | Priority1 | FALSE |  |  |  |  | Low critical warning battery system
|  | Digital | Hybrid.PMS.ESSWarningWord0 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 0 |  |  | ESS in manual mode
|  | Digital | Hybrid.PMS.ESSWarningWord1 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 1 |  |  | String1 disconnected
|  | Digital | Hybrid.PMS.ESSWarningWord2 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 2 |  |  | String2 disconnected
|  | Digital | Hybrid.PMS.ESSWarningWord3 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 3 |  |  | Grid drive alarm, check display
|  | Digital | Hybrid.PMS.ESSWarningWord4 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 4 |  |  | Temerature high L1 transformer
|  | Digital | Hybrid.PMS.ESSWarningWord5 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 5 |  |  | Temerature high L2 transformer
|  | Digital | Hybrid.PMS.ESSWarningWord6 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 6 |  |  | Temerature high L3 transformer
|  | Digital | Hybrid.PMS.ESSWarningWord7 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 7 |  |  | Temperature delta high transformer
|  | Digital | Hybrid.PMS.ESSWarningWord8 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 8 |  |  | State of charge low warn ESS
|  | Digital | Hybrid.PMS.ESSWarningWord9 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 9 |  |  | Ambient temperature in battery room high
|  | Digital | Hybrid.PMS.ESSWarningWord10 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 10 |  |  | Cell voltage low ESS
|  | Digital | Hybrid.PMS.ESSWarningWord11 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 11 |  |  | Cell voltage high ESS
|  | Digital | Hybrid.PMS.ESSWarningWord12 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 12 |  |  | State of charge too high ESS
|  | Digital | Hybrid.PMS.ESSWarningWord14 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 14 |  |  | Pre-fault warning from batteries, see other faults/warnings for more info
|  | Digital | Hybrid.PMS.ESSWarningWord15 | Hybrid.ESS.ESS_Warning |  | High | Priority2 | FALSE |  | 15 |  |  | Battery temperature high
|  | Digital | Hybrid.PMS.ESSWarning2Word1 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 0 |  |  | Spare1
|  | Digital | Hybrid.PMS.ESSWarning2Word2 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 1 |  |  | Spare2
|  | Digital | Hybrid.PMS.ESSWarning2Word3 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 2 |  |  | Spare3
|  | Digital | Hybrid.PMS.ESSWarning2Word4 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 3 |  |  | Spare4
|  | Digital | Hybrid.PMS.ESSWarning2Word5 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 4 |  |  | Spare5
|  | Digital | Hybrid.PMS.ESSWarning2Word6 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 5 |  |  | Spare6
|  | Digital | Hybrid.PMS.ESSWarning2Word7 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 6 |  |  | Spare7
|  | Digital | Hybrid.PMS.ESSWarning2Word8 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 7 |  |  | Spare8
|  | Digital | Hybrid.PMS.ESSWarning2Word9 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 8 |  |  | Spare9
|  | Digital | Hybrid.PMS.ESSWarning2Word10 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 9 |  |  | Spare10
|  | Digital | Hybrid.PMS.ESSWarning2Word11 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 10 |  |  | Spare11
|  | Digital | Hybrid.PMS.ESSWarning2Word12 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 11 |  |  | Spare12
|  | Digital | Hybrid.PMS.ESSWarning2Word13 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 12 |  |  | Spare13
|  | Digital | Hybrid.PMS.ESSWarning2Word14 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 13 |  |  | Spare14
|  | Digital | Hybrid.PMS.ESSWarning2Word15 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 14 |  |  | Spare15
|  | Digital | Hybrid.PMS.ESSWarning2Word16 | Hybrid.ESS.ESS_Warning1 |  | High | Priority2 | FALSE |  | 15 |  |  | Spare16
|  | Digital | Hybrid.PMS.ESSFaultWord0 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 0 |  |  | Emergency stop activated ESS
|  | Digital | Hybrid.PMS.ESSFaultWord1 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 1 |  |  | Grid drive tripped
|  | Digital | Hybrid.PMS.ESSFaultWord2 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 2 |  |  | BMS common fault
|  | Digital | Hybrid.PMS.ESSFaultWord3 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 3 |  |  | Temperature high high L1 transformer
|  | Digital | Hybrid.PMS.ESSFaultWord4 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 4 |  |  | Temperature high high L2 transformer
|  | Digital | Hybrid.PMS.ESSFaultWord5 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 5 |  |  | Temperature high high L3 transformer
|  | Digital | Hybrid.PMS.ESSFaultWord6 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 6 |  |  | Watchdog timeout, communication lost with EMS
|  | Digital | Hybrid.PMS.ESSFaultWord7 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 7 |  |  | Grid drive startup timeout
|  | Digital | Hybrid.PMS.ESSFaultWord8 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 8 |  |  | Hybrid breaker tripped on-load
|  | Digital | Hybrid.PMS.ESSFaultWord9 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 9 |  |  | Temperature delta high high transformer
|  | Digital | Hybrid.PMS.ESSFaultWord10 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 10 |  |  | Insulation monitor fault 1
|  | Digital | Hybrid.PMS.ESSFaultWord11 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 11 |  |  | Insulation monitor fault 2
|  | Digital | Hybrid.PMS.ESSFaultWord12 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 12 |  |  | State of charge too low fault ESS
|  | Digital | Hybrid.PMS.ESSFaultWord13 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 13 |  |  | Drive not in auto/remote
|  | Digital | Hybrid.PMS.ESSFaultWord14 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 14 |  |  | ESS breaker failed to close
|  | Digital | Hybrid.PMS.ESSFaultWord15 | Hybrid.ESS.ESS_Fault |  | High | Priority1 | FALSE |  | 15 |  |  | Failed to sync
|  | Digital | Hybrid.PMS.ESSFault2Word1 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 0 |  |  | ESS breaker failed to open
|  | Digital | Hybrid.PMS.ESSFault2Word2 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 1 |  |  | Spare17
|  | Digital | Hybrid.PMS.ESSFault2Word3 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 2 |  |  | Spare18
|  | Digital | Hybrid.PMS.ESSFault2Word4 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 3 |  |  | Spare19
|  | Digital | Hybrid.PMS.ESSFault2Word5 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 4 |  |  | Spare20
|  | Digital | Hybrid.PMS.ESSFault2Word6 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 5 |  |  | Spare21
|  | Digital | Hybrid.PMS.ESSFault2Word7 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 6 |  |  | Spare22
|  | Digital | Hybrid.PMS.ESSFault2Word8 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 7 |  |  | Spare23
|  | Digital | Hybrid.PMS.ESSFault2Word9 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 8 |  |  | Spare24
|  | Digital | Hybrid.PMS.ESSFault2Word10 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 9 |  |  | Spare25
|  | Digital | Hybrid.PMS.ESSFault2Word11 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 10 |  |  | Spare26
|  | Digital | Hybrid.PMS.ESSFault2Word12 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 11 |  |  | Spare27
|  | Digital | Hybrid.PMS.ESSFault2Word13 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 12 |  |  | Spare28
|  | Digital | Hybrid.PMS.ESSFault2Word14 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 13 |  |  | Spare29
|  | Digital | Hybrid.PMS.ESSFault2Word15 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 14 |  |  | Spare30
|  | Digital | Hybrid.PMS.ESSFault2Word16 | Hybrid.ESS.ESS_Fault1 |  | High | Priority1 | FALSE |  | 15 |  |  | Spare31
|  | Digital | Genset1.Generator.Fault | Genset1.Generator.Fault |  | High | Priority1 | FALSE |  |  |  |  | Genset 1 fault
|  | Digital | Genset1.Generator.warningWord0 | Genset1.Generator.WarningWord |  | High | Priority2 | FALSE |  | 0 |  |  | Gen1 Failed to deload
|  | Digital | Genset1.Generator.warningWord2 | Genset1.Generator.WarningWord |  | High | Priority2 | FALSE |  | 2 |  |  | Gen1 Restarting
|  | Digital | Genset1.Generator.warningWord3 | Genset1.Generator.WarningWord |  | High | Priority2 | FALSE |  | 3 |  |  | Gen1 Ambient Temperature high
|  | Digital | Genset1.Generator.warningWord4 | Genset1.Generator.WarningWord |  | High | Priority2 | FALSE |  | 4 |  |  | Gen1 Overload warning
|  | Digital | Genset1.Generator.warningWord5 | Genset1.Generator.WarningWord |  | High | Priority2 | FALSE |  | 5 |  |  | Gen1 Recovering
|  | Digital | Genset1.Generator.alarmWord0 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 0 |  |  | Gen1 Failed to start
|  | Digital | Genset1.Generator.alarmWord1 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 1 |  |  | Gen1 Synchronization fault
|  | Digital | Genset1.Generator.alarmWord2 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 2 |  |  | Gen1 Failed to disconnect generator breaker
|  | Digital | Genset1.Generator.alarmWord3 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 3 |  |  | Gen1 Failed to stop generator
|  | Digital | Genset1.Generator.alarmWord4 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 4 |  |  | Gen1 Fault from generator panel
|  | Digital | Genset1.Generator.alarmWord5 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 5 |  |  | Gen1 Genset Autorecovery failed
|  | Digital | Genset1.Generator.alarmWord6 | Genset1.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 6 |  |  | Gen1 On-load fault
|  | Digital | Genset2.Generator.Fault | Genset2.Generator.Fault |  | High | Priority1 | FALSE |  |  |  |  | Genset 2 fault
|  | Digital | Genset2.Generator.warningWord0 | Genset2.Generator.WarningWord |  | High | Priority2 | FALSE |  | 0 |  |  | Gen2 Failed to deload
|  | Digital | Genset2.Generator.warningWord2 | Genset2.Generator.WarningWord |  | High | Priority2 | FALSE |  | 2 |  |  | Gen2 Restarting
|  | Digital | Genset2.Generator.warningWord3 | Genset2.Generator.WarningWord |  | High | Priority2 | FALSE |  | 3 |  |  | Gen2 Ambient Temperature high
|  | Digital | Genset2.Generator.warningWord4 | Genset2.Generator.WarningWord |  | High | Priority2 | FALSE |  | 4 |  |  | Gen2 Overload warning
|  | Digital | Genset2.Generator.warningWord5 | Genset2.Generator.WarningWord |  | High | Priority2 | FALSE |  | 5 |  |  | Gen2 Recovering
|  | Digital | Genset2.Generator.alarmWord0 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 0 |  |  | Gen2 Failed to start
|  | Digital | Genset2.Generator.alarmWord1 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 1 |  |  | Gen2 Synchronization fault
|  | Digital | Genset2.Generator.alarmWord2 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 2 |  |  | Gen2 Failed to disconnect generator breaker
|  | Digital | Genset2.Generator.alarmWord3 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 3 |  |  | Gen2 Failed to stop generator
|  | Digital | Genset2.Generator.alarmWord4 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 4 |  |  | Gen2 Fault from generator panel
|  | Digital | Genset2.Generator.alarmWord5 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 5 |  |  | Gen2 Genset Autorecovery failed
|  | Digital | Genset2.Generator.alarmWord6 | Genset2.Generator.AlarmWord |  | High | Priority1 | FALSE |  | 6 |  |  | Gen2 On-load fault
|  | Digital | Hybrid.PMS.Blackout | Hybrid.EMS.Blackout |  | High | Priority1 | FALSE |  | 0 |  |  | Barge BLACKOUT