## EMS modbus
Sheet type |  | Modbus RTU Master |  | Data access list
Sheet name |  | Generatormålinger/EMS |  | Slaveaddresse | Register address | Register group | System | Sensor | Measurement | Tag | Fieldbus data type | Type | Formatter | Unit | Range high | Range low | Description | Update interval | Historian | Function code | Data length | Scale factor | Decimals
Data port |  | EMS |  | 1 | 13089 | Measurement | Hybrid | ESS | PhaseVoltage | Hybrid.ESS.PhaseVoltage | ushort | single |  |  |  |  | Phase voltage |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 13092 | Measurement | Hybrid | ESS | ReactivePower | Hybrid.ESS.ReactivePower | short | single |  |  |  |  | Reactive power |  | TRUE | 3 |  | 0.1 | 1
Modbus RTU Master settings |  |  |  | 1 | 13093 | Measurement | Hybrid | ESS | Current | Hybrid.ESS.Current | short | single |  |  |  |  | Current |  | TRUE | 3 |  | 0.1 | 1
Protocol mode |  |  | TCP | 1 | 13094 | Measurement | Hybrid | ESS | CosPhi | Hybrid.ESS.CosPhi | ushort | single |  |  |  |  | Cos phi |  | TRUE | 3 |  | 0.01 | 2
Request timeout |  |  | 2000 | 1 | 13095 | Measurement | Hybrid | ESS | ApparentPower | Hybrid.ESS.ApparentPower | short | single |  |  |  |  | Apparent power |  | TRUE | 3 |  | 0.1 | 1
Request timeout |  |  | 100 | 1 | 13096 | Measurement | Hybrid | ESS | TotalHarmonicDistortion | Hybrid.ESS.TotalHarmonicDistortion | ushort | single |  |  |  |  | Total harmonic distortion |  | TRUE | 3 |  | 0.01 | 2
Slave byte order settings |  |  |  | 1 | 13188 | Measurement | Hybrid | ESS | BargeLoad | Hybrid.ESS.BargeLoad | ushort | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
Slave no. | 16 bit | 32 bit | String | 1 | 13189.15 | Measurement | Hybrid | Ems | Watchdog | Hybrid.Ems.Watchdog | bool | [5 empty] | EMS watchdog to detect network loss |  | TRUE | 3
1 | Modbus | Modbus | Modbus | 1 | 12289 | Measurement | Genset1 | Generator | Voltage | Genset1.Generator.Voltage | ushort | single |  | V |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12290 | Measurement | Genset1 | Generator | Frequency | Genset1.Generator.Frequency | ushort | single |  | Hz |  |  |  |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12291 | Measurement | Genset1 | Generator | ActivePowerTotal | Genset1.Generator.ActivePowerTotal | short | single |  | kW |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12294 | Measurement | Genset1 | Generator | CosPhi | Genset1.Generator.CosPhi | ushort | single | [6 empty] | TRUE | 3 |  | 0.001 | 3
|  |  |  | 1 | 12295 | Measurement | Genset1 | Generator | ApparentPowerTotal | Genset1.Generator.ApparentPowerTotal | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12296 | Measurement | Genset1 | Generator | TotalHarmonicDistortion | Genset1.Generator.TotalHarmonicDistortion | ushort | single | [6 empty] | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12297 | Measurement | Genset1 | Generator | AmbientTemperature | Genset1.Generator.AmbientTemperature | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 2
|  |  |  | 1 | 12288 | Measurement | Genset1 | Generator | Ready | Genset1.Generator.Ready | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12288.1 | Measurement | Genset1 | Generator | Running | Genset1.Generator.Running | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12288.2 | Measurement | Genset1 | Generator | Warning | Genset1.Generator.Warning | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12288.3 | Measurement | Genset1 | Generator | Fault | Genset1.Generator.Fault | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12299 | Measurement | Genset1 | Generator | CurrentL1 | Genset1.Generator.CurrentL1 | ushort | single |  | A |  |  | Current L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12300 | Measurement | Genset1 | Generator | CurrentL2 | Genset1.Generator.CurrentL2 | ushort | single |  | A |  |  | Current L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12301 | Measurement | Genset1 | Generator | CurrentL3 | Genset1.Generator.CurrentL3 | ushort | single |  | A |  |  | Current L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12302 | Measurement | Genset1 | Generator | VoltageL1L3 | Genset1.Generator.VoltageL1L3 | ushort | single |  | V |  |  | Voltage between L1-L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12303 | Measurement | Genset1 | Generator | VoltageL1L2 | Genset1.Generator.VoltageL1L2 | ushort | single |  | V |  |  | Voltage between L2-L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12304 | Measurement | Genset1 | Generator | VoltageL2L3 | Genset1.Generator.VoltageL2L3 | ushort | single |  | V |  |  | Voltage between L3-L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12305 | Measurement | Genset1 | Generator | VoltageL1N | Genset1.Generator.VoltageL1N | ushort | single |  | V |  |  | Voltage between L1-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12306 | Measurement | Genset1 | Generator | VoltageL2N | Genset1.Generator.VoltageL2N | ushort | single |  | V |  |  | Voltage between L2-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12307 | Measurement | Genset1 | Generator | VoltageL3N | Genset1.Generator.VoltageL3N | ushort | single |  | V |  |  | Voltage between L3-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12308 | Measurement | Genset1 | Generator | FrequencyL1 | Genset1.Generator.FrequencyL1 | ushort | single |  | Hz |  |  | Frequency phase L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12309 | Measurement | Genset1 | Generator | FrequencyL2 | Genset1.Generator.FrequencyL2 | ushort | single |  | Hz |  |  | Frequency phase L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12310 | Measurement | Genset1 | Generator | FrequencyL3 | Genset1.Generator.FrequencyL3 | ushort | single |  | Hz |  |  | Frequency phase L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12311 | Measurement | Genset1 | Generator | ActivePowerL1 | Genset1.Generator.ActivePowerL1 | ushort | single |  | kW |  |  | Active power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12312 | Measurement | Genset1 | Generator | ActivePowerL2 | Genset1.Generator.ActivePowerL2 | ushort | single |  | kW |  |  | Active power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12313 | Measurement | Genset1 | Generator | ActivePowerL3 | Genset1.Generator.ActivePowerL3 | ushort | single |  | kW |  |  | Active power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12314 | Measurement | Genset1 | Generator | ReactivePowerL1 | Genset1.Generator.ReactivePowerL1 | ushort | single |  | kVAr |  |  | Reactive power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12315 | Measurement | Genset1 | Generator | ReactivePowerL2 | Genset1.Generator.ReactivePowerL2 | ushort | single |  | kVAr |  |  | Reactive power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12316 | Measurement | Genset1 | Generator | ReactivePowerL3 | Genset1.Generator.ReactivePowerL3 | ushort | single |  | kVAr |  |  | Reactive power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12317 | Measurement | Genset1 | Generator | ApparentPowerL1 | Genset1.Generator.ApparentPowerL1 | ushort | single |  | kVA |  |  | Apparent power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12318 | Measurement | Genset1 | Generator | ApparentPowerL2 | Genset1.Generator.ApparentPowerL2 | ushort | single |  | kVA |  |  | Apparent power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12319 | Measurement | Genset1 | Generator | ApparentPowerL3 | Genset1.Generator.ApparentPowerL3 | ushort | single |  | kVA |  |  | Apparent power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12320 | Measurement | Genset1 | Generator | PhaseAngleL1 | Genset1.Generator.PhaseAngleL1 | ushort | single |  | ° |  |  | Phase angle L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12321 | Measurement | Genset1 | Generator | PhaseAngleL2 | Genset1.Generator.PhaseAngleL2 | ushort | single |  | ° |  |  | Phase angle L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12322 | Measurement | Genset1 | Generator | PhaseAngleL3 | Genset1.Generator.PhaseAngleL3 | ushort | single |  | ° |  |  | Phase angle L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12323 | Measurement | Genset1 | Generator | CosPhiL1 | Genset1.Generator.CosPhiL1 | ushort | single |  |  |  |  | Cos phi L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12324 | Measurement | Genset1 | Generator | CosPhiL2 | Genset1.Generator.CosPhiL2 | ushort | single |  |  |  |  | Cos phi L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12325 | Measurement | Genset1 | Generator | CosPhiL3 | Genset1.Generator.CosPhiL3 | ushort | single |  |  |  |  | Cos phi L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12326 | Measurement | Genset1 | Generator | PowerFactorL1 | Genset1.Generator.PowerFactorL1 | ushort | single |  |  |  |  | Power factor L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12327 | Measurement | Genset1 | Generator | PowerFactorL2 | Genset1.Generator.PowerFactorL2 | ushort | single |  |  |  |  | Power factor L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12328 | Measurement | Genset1 | Generator | PowerFactorL3 | Genset1.Generator.PowerFactorL3 | ushort | single |  |  |  |  | Power factor L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 13288 | Measurement | Hybrid | ESS | G1Setpoint100kWe | Hybrid.ESS.G1Setpoint100kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13289 | Measurement | Hybrid | ESS | G1Setpoint80kWe | Hybrid.ESS.G1Setpoint80kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13290 | Measurement | Hybrid | ESS | G1SetpointEco | Hybrid.ESS.G1SetpointEco | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13291 | Measurement | Hybrid | Ems | G1ControlWord | Hybrid.Ems.G1ControlWord | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13292 | Measurement | Hybrid | Ems | G1ShaftLoadPercentage | Hybrid.Ems.G1ShaftLoadPercentage | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 12389 | Measurement | Genset2 | Generator | Voltage | Genset2.Generator.Voltage | ushort | single |  | V |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12390 | Measurement | Genset2 | Generator | Frequency | Genset2.Generator.Frequency | ushort | single |  | Hz |  |  |  |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12391 | Measurement | Genset2 | Generator | ActivePowerTotal | Genset2.Generator.ActivePowerTotal | short | single |  | kW |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12394 | Measurement | Genset2 | Generator | CosPhi | Genset2.Generator.CosPhi | ushort | single | [6 empty] | TRUE | 3 |  | 0.001 | 3
|  |  |  | 1 | 12395 | Measurement | Genset2 | Generator | ApparentPowerTotal | Genset2.Generator.ApparentPowerTotal | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12396 | Measurement | Genset2 | Generator | TotalHarmonicDistortion | Genset2.Generator.TotalHarmonicDistortion | ushort | single | [6 empty] | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12397 | Measurement | Genset2 | Generator | AmbientTemperature | Genset2.Generator.AmbientTemperature | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 2
|  |  |  | 1 | 12388 | Measurement | Genset2 | Generator | Ready | Genset2.Generator.Ready | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12388.1 | Measurement | Genset2 | Generator | Running | Genset2.Generator.Running | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12388.2 | Measurement | Genset2 | Generator | Warning | Genset2.Generator.Warning | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12388.3 | Measurement | Genset2 | Generator | Fault | Genset2.Generator.Fault | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12399 | Measurement | Genset2 | Generator | CurrentL1 | Genset2.Generator.CurrentL1 | ushort | single |  | A |  |  | Current L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12400 | Measurement | Genset2 | Generator | CurrentL2 | Genset2.Generator.CurrentL2 | ushort | single |  | A |  |  | Current L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12401 | Measurement | Genset2 | Generator | CurrentL3 | Genset2.Generator.CurrentL3 | ushort | single |  | A |  |  | Current L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12402 | Measurement | Genset2 | Generator | VoltageL1L3 | Genset2.Generator.VoltageL1L3 | ushort | single |  | V |  |  | Voltage between L1-L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12403 | Measurement | Genset2 | Generator | VoltageL1L2 | Genset2.Generator.VoltageL1L2 | ushort | single |  | V |  |  | Voltage between L2-L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12404 | Measurement | Genset2 | Generator | VoltageL2L3 | Genset2.Generator.VoltageL2L3 | ushort | single |  | V |  |  | Voltage between L3-L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12405 | Measurement | Genset2 | Generator | VoltageL1N | Genset2.Generator.VoltageL1N | ushort | single |  | V |  |  | Voltage between L1-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12406 | Measurement | Genset2 | Generator | VoltageL2N | Genset2.Generator.VoltageL2N | ushort | single |  | V |  |  | Voltage between L2-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12407 | Measurement | Genset2 | Generator | VoltageL3N | Genset2.Generator.VoltageL3N | ushort | single |  | V |  |  | Voltage between L3-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12408 | Measurement | Genset2 | Generator | FrequencyL1 | Genset2.Generator.FrequencyL1 | ushort | single |  | Hz |  |  | Frequency phase L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12409 | Measurement | Genset2 | Generator | FrequencyL2 | Genset2.Generator.FrequencyL2 | ushort | single |  | Hz |  |  | Frequency phase L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12410 | Measurement | Genset2 | Generator | FrequencyL3 | Genset2.Generator.FrequencyL3 | ushort | single |  | Hz |  |  | Frequency phase L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12411 | Measurement | Genset2 | Generator | ActivePowerL1 | Genset2.Generator.ActivePowerL1 | ushort | single |  | kW |  |  | Active power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12412 | Measurement | Genset2 | Generator | ActivePowerL2 | Genset2.Generator.ActivePowerL2 | ushort | single |  | kW |  |  | Active power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12413 | Measurement | Genset2 | Generator | ActivePowerL3 | Genset2.Generator.ActivePowerL3 | ushort | single |  | kW |  |  | Active power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12414 | Measurement | Genset2 | Generator | ReactivePowerL1 | Genset2.Generator.ReactivePowerL1 | ushort | single |  | kVAr |  |  | Reactive power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12415 | Measurement | Genset2 | Generator | ReactivePowerL2 | Genset2.Generator.ReactivePowerL2 | ushort | single |  | kVAr |  |  | Reactive power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12416 | Measurement | Genset2 | Generator | ReactivePowerL3 | Genset2.Generator.ReactivePowerL3 | ushort | single |  | kVAr |  |  | Reactive power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12417 | Measurement | Genset2 | Generator | ApparentPowerL1 | Genset2.Generator.ApparentPowerL1 | ushort | single |  | kVA |  |  | Apparent power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12418 | Measurement | Genset2 | Generator | ApparentPowerL2 | Genset2.Generator.ApparentPowerL2 | ushort | single |  | kVA |  |  | Apparent power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12419 | Measurement | Genset2 | Generator | ApparentPowerL3 | Genset2.Generator.ApparentPowerL3 | ushort | single |  | kVA |  |  | Apparent power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12420 | Measurement | Genset2 | Generator | PhaseAngleL1 | Genset2.Generator.PhaseAngleL1 | ushort | single |  | ° |  |  | Phase angle L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12421 | Measurement | Genset2 | Generator | PhaseAngleL2 | Genset2.Generator.PhaseAngleL2 | ushort | single |  | ° |  |  | Phase angle L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12422 | Measurement | Genset2 | Generator | PhaseAngleL3 | Genset2.Generator.PhaseAngleL3 | ushort | single |  | ° |  |  | Phase angle L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12423 | Measurement | Genset2 | Generator | CosPhiL1 | Genset2.Generator.CosPhiL1 | ushort | single |  |  |  |  | Cos phi L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12424 | Measurement | Genset2 | Generator | CosPhiL2 | Genset2.Generator.CosPhiL2 | ushort | single |  |  |  |  | Cos phi L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12425 | Measurement | Genset2 | Generator | CosPhiL3 | Genset2.Generator.CosPhiL3 | ushort | single |  |  |  |  | Cos phi L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12426 | Measurement | Genset2 | Generator | PowerFactorL1 | Genset2.Generator.PowerFactorL1 | ushort | single |  |  |  |  | Power factor L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12427 | Measurement | Genset2 | Generator | PowerFactorL2 | Genset2.Generator.PowerFactorL2 | ushort | single |  |  |  |  | Power factor L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12428 | Measurement | Genset2 | Generator | PowerFactorL3 | Genset2.Generator.PowerFactorL3 | ushort | single |  |  |  |  | Power factor L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 13388 | Measurement | Hybrid | ESS | G2Setpoint100kWe | Hybrid.ESS.G2Setpoint100kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13389 | Measurement | Hybrid | ESS | G2Setpoint80kWe | Hybrid.ESS.G2Setpoint80kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13390 | Measurement | Hybrid | ESS | G2SetpointEco | Hybrid.ESS.G2SetpointEco | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13391 | Measurement | Hybrid | Ems | G2ShaftLoadPercentage | Hybrid.Ems.G2ShaftLoadPercentage | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13392 | Measurement | Hybrid | Ems | G2ControlWord | Hybrid.Ems.G2ControlWord | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 12489 | Measurement | Genset3 | Generator | Voltage | Genset3.Generator.Voltage | ushort | single |  | V |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12490 | Measurement | Genset3 | Generator | Frequency | Genset3.Generator.Frequency | ushort | single |  | Hz |  |  |  |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12491 | Measurement | Genset3 | Generator | ActivePowerTotal | Genset3.Generator.ActivePowerTotal | short | single |  | kW |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12494 | Measurement | Genset3 | Generator | CosPhi | Genset3.Generator.CosPhi | ushort | single | [6 empty] | TRUE | 3 |  | 0.001 | 3
|  |  |  | 1 | 12495 | Measurement | Genset3 | Generator | ApparentPowerTotal | Genset3.Generator.ApparentPowerTotal | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12496 | Measurement | Genset3 | Generator | TotalHarmonicDistortion | Genset3.Generator.TotalHarmonicDistortion | ushort | single | [6 empty] | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12497 | Measurement | Genset3 | Generator | AmbientTemperature | Genset3.Generator.AmbientTemperature | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 2
|  |  |  | 1 | 12488 | Measurement | Genset3 | Generator | Ready | Genset3.Generator.Ready | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12488.1 | Measurement | Genset3 | Generator | Running | Genset3.Generator.Running | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12488.2 | Measurement | Genset3 | Generator | Warning | Genset3.Generator.Warning | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12488.3 | Measurement | Genset3 | Generator | Fault | Genset3.Generator.Fault | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 12499 | Measurement | Genset3 | Generator | CurrentL1 | Genset3.Generator.CurrentL1 | ushort | single |  | A |  |  | Current L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12500 | Measurement | Genset3 | Generator | CurrentL2 | Genset3.Generator.CurrentL2 | ushort | single |  | A |  |  | Current L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12501 | Measurement | Genset3 | Generator | CurrentL3 | Genset3.Generator.CurrentL3 | ushort | single |  | A |  |  | Current L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12502 | Measurement | Genset3 | Generator | VoltageL1L3 | Genset3.Generator.VoltageL1L3 | ushort | single |  | V |  |  | Voltage between L1-L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12503 | Measurement | Genset3 | Generator | VoltageL1L2 | Genset3.Generator.VoltageL1L2 | ushort | single |  | V |  |  | Voltage between L2-L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12504 | Measurement | Genset3 | Generator | VoltageL2L3 | Genset3.Generator.VoltageL2L3 | ushort | single |  | V |  |  | Voltage between L3-L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12505 | Measurement | Genset3 | Generator | VoltageL1N | Genset3.Generator.VoltageL1N | ushort | single |  | V |  |  | Voltage between L1-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12506 | Measurement | Genset3 | Generator | VoltageL2N | Genset3.Generator.VoltageL2N | ushort | single |  | V |  |  | Voltage between L2-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12507 | Measurement | Genset3 | Generator | VoltageL3N | Genset3.Generator.VoltageL3N | ushort | single |  | V |  |  | Voltage between L3-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12508 | Measurement | Genset3 | Generator | FrequencyL1 | Genset3.Generator.FrequencyL1 | ushort | single |  | Hz |  |  | Frequency phase L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12509 | Measurement | Genset3 | Generator | FrequencyL2 | Genset3.Generator.FrequencyL2 | ushort | single |  | Hz |  |  | Frequency phase L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12510 | Measurement | Genset3 | Generator | FrequencyL3 | Genset3.Generator.FrequencyL3 | ushort | single |  | Hz |  |  | Frequency phase L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12511 | Measurement | Genset3 | Generator | ActivePowerL1 | Genset3.Generator.ActivePowerL1 | ushort | single |  | kW |  |  | Active power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12512 | Measurement | Genset3 | Generator | ActivePowerL2 | Genset3.Generator.ActivePowerL2 | ushort | single |  | kW |  |  | Active power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12513 | Measurement | Genset3 | Generator | ActivePowerL3 | Genset3.Generator.ActivePowerL3 | ushort | single |  | kW |  |  | Active power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12514 | Measurement | Genset3 | Generator | ReactivePowerL1 | Genset3.Generator.ReactivePowerL1 | ushort | single |  | kVAr |  |  | Reactive power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12515 | Measurement | Genset3 | Generator | ReactivePowerL2 | Genset3.Generator.ReactivePowerL2 | ushort | single |  | kVAr |  |  | Reactive power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12516 | Measurement | Genset3 | Generator | ReactivePowerL3 | Genset3.Generator.ReactivePowerL3 | ushort | single |  | kVAr |  |  | Reactive power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12517 | Measurement | Genset3 | Generator | ApparentPowerL1 | Genset3.Generator.ApparentPowerL1 | ushort | single |  | kVA |  |  | Apparent power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12518 | Measurement | Genset3 | Generator | ApparentPowerL2 | Genset3.Generator.ApparentPowerL2 | ushort | single |  | kVA |  |  | Apparent power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12519 | Measurement | Genset3 | Generator | ApparentPowerL3 | Genset3.Generator.ApparentPowerL3 | ushort | single |  | kVA |  |  | Apparent power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12520 | Measurement | Genset3 | Generator | PhaseAngleL1 | Genset3.Generator.PhaseAngleL1 | ushort | single |  | ° |  |  | Phase angle L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12521 | Measurement | Genset3 | Generator | PhaseAngleL2 | Genset3.Generator.PhaseAngleL2 | ushort | single |  | ° |  |  | Phase angle L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12522 | Measurement | Genset3 | Generator | PhaseAngleL3 | Genset3.Generator.PhaseAngleL3 | ushort | single |  | ° |  |  | Phase angle L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12523 | Measurement | Genset3 | Generator | CosPhiL1 | Genset3.Generator.CosPhiL1 | ushort | single |  |  |  |  | Cos phi L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12524 | Measurement | Genset3 | Generator | CosPhiL2 | Genset3.Generator.CosPhiL2 | ushort | single |  |  |  |  | Cos phi L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12525 | Measurement | Genset3 | Generator | CosPhiL3 | Genset3.Generator.CosPhiL3 | ushort | single |  |  |  |  | Cos phi L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12526 | Measurement | Genset3 | Generator | PowerFactorL1 | Genset3.Generator.PowerFactorL1 | ushort | single |  |  |  |  | Power factor L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12527 | Measurement | Genset3 | Generator | PowerFactorL2 | Genset3.Generator.PowerFactorL2 | ushort | single |  |  |  |  | Power factor L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12528 | Measurement | Genset3 | Generator | PowerFactorL3 | Genset3.Generator.PowerFactorL3 | ushort | single |  |  |  |  | Power factor L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 13488 | Measurement | Hybrid | ESS | G3Setpoint100kWe | Hybrid.ESS.G3Setpoint100kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13489 | Measurement | Hybrid | ESS | G3Setpoint80kWe | Hybrid.ESS.G3Setpoint80kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13490 | Measurement | Hybrid | ESS | G3SetpointEco | Hybrid.ESS.G3SetpointEco | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13491 | Measurement | Hybrid | Ems | G3ShaftLoadPercentage | Hybrid.Ems.G3ShaftLoadPercentage | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 13492 | Measurement | Hybrid | Ems | G3ControlWord | Hybrid.Ems.G3ControlWord | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 12343 | Measurement | Genset1 | Generator | WarningWord | Genset1.Generator.WarningWord | ushort | [5 empty] | Warning word gen1 |  | TRUE | 3
|  |  |  | 1 | 12344 | Measurement | Genset1 | Generator | AlarmWord | Genset1.Generator.AlarmWord | ushort | [5 empty] | Alarm word gen1 |  | TRUE | 3
|  |  |  | 1 | 12443 | Measurement | Genset2 | Generator | WarningWord | Genset2.Generator.WarningWord | ushort | [5 empty] | Warning word gen2 |  | TRUE | 3
|  |  |  | 1 | 12444 | Measurement | Genset2 | Generator | AlarmWord | Genset2.Generator.AlarmWord | ushort | [5 empty] | Alarm word gen2 |  | TRUE | 3
|  |  |  | 1 | 12543 | Measurement | Genset3 | Generator | WarningWord | Genset3.Generator.WarningWord | ushort | [5 empty] | Warning word gen3 |  | TRUE | 3
|  |  |  | 1 | 12544 | Measurement | Genset3 | Generator | AlarmWord | Genset3.Generator.AlarmWord | ushort | [5 empty] | Alarm word gen3 |  | TRUE | 3
|  |  |  | 1 | 12345 | Measurement | Genset1 | Generator | Priority | Genset1.Generator.Priority | ushort | [5 empty] | Genset priority |  | TRUE | 3
|  |  |  | 1 | 12445 | Measurement | Genset2 | Generator | Priority | Genset2.Generator.Priority | ushort | [5 empty] | Genset priority |  | TRUE | 3
|  |  |  | 1 | 12545 | Measurement | Genset3 | Generator | Priority | Genset3.Generator.Priority | ushort | [5 empty] | Genset priority |  | TRUE | 3
|  |  |  | 1 | 13190 | Measurement | Hybrid | EMS | Blackout | Hybrid.EMS.Blackout | ushort | [5 empty] | EMS blackout |  | TRUE | 3
|  |  |  | 1 | 13191 | Measurement | Hybrid | EMS | Charging | Hybrid.EMS.Charging | ushort | [5 empty] | EMS charge mode |  | TRUE | 3
|  |  |  | 1 | 13192 | Parameter | a | EMS | PLC_SW_Version | a.EMS.PLC_SW_Version | ushort | [5 empty] | EMS PLC SW Verison |  | TRUE | 3
|  |  |  | 1 | 12288 | Parameter | a | EMS | HMI_SW_Version | a.EMS.HMI_SW_Version | ushort | [5 empty] | EMS HMI SW Verison |  | TRUE | 3
|  |  |  | 1 | 12288 | Measurement | a | Nexus | Config_version | a.Nexus.Config_version | ushort | [5 empty] | Config version |  | TRUE | 3