## EMS modbus
Sheet type |  | Modbus RTU Master |  | Data access list
Sheet name |  | Generatormålinger/EMS |  | Slaveaddresse | Register address | Register group | System | Sensor | Measurement | Tag | Fieldbus data type | Type | Formatter | Unit | Range high | Range low | Description | Update interval | Historian | Function code | Data length | Scale factor | Decimals
Data port |  | EMS |  | 1 | 1 | Measurement | Genset1 | Generator | Voltage | Genset1.Generator.Voltage | ushort | single |  | V |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 2 | Measurement | Genset1 | Generator | Frequency | Genset1.Generator.Frequency | ushort | single |  | Hz |  |  |  |  | TRUE | 3 |  | 0.01 | 2
Modbus RTU Master settings |  |  |  | 1 | 3 | Measurement | Genset1 | Generator | ActivePowerTotal | Genset1.Generator.ActivePowerTotal | short | single |  | kW |  |  |  |  | TRUE | 3 |  | 0.1 | 1
Protocol mode |  |  | TCP | 1 | 6 | Measurement | Genset1 | Generator | CosPhi | Genset1.Generator.CosPhi | ushort | single | [6 empty] | TRUE | 3 |  | 0.001 | 3
Request timeout |  |  | 2000 | 1 | 7 | Measurement | Genset1 | Generator | ApparentPowerTotal | Genset1.Generator.ApparentPowerTotal | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
Request pause |  |  | 100 | 1 | 8 | Measurement | Genset1 | Generator | TotalHarmonicDistortion | Genset1.Generator.TotalHarmonicDistortion | ushort | single | [6 empty] | TRUE | 3 |  | 0.01 | 2
Slave byte order settings |  |  |  | 1 | 9 | Measurement | Genset1 | Generator | AmbientTemperature | Genset1.Generator.AmbientTemperature | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
Slave no. | 16 bit | 32 bit | String | 1 | 801 | Measurement | Hybrid | ESS | PhaseVoltage | Hybrid.ESS.PhaseVoltage | ushort | single |  |  |  |  | Phase voltage |  | TRUE | 3 |  | 0.1 | 1
1 | Modbus | Modbus | Modbus | 1 | 804 | Measurement | Hybrid | ESS | ReactivePower | Hybrid.ESS.ReactivePower | short | single |  |  |  |  | Reactive power |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 805 | Measurement | Hybrid | ESS | Current | Hybrid.ESS.Current | ushort | [5 empty] | Current |  | TRUE | 3
|  |  |  | 1 | 806 | Measurement | Hybrid | ESS | CosPhi | Hybrid.ESS.CosPhi | ushort | single |  |  |  |  | Cos phi |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 807 | Measurement | Hybrid | ESS | ApparentPower | Hybrid.ESS.ApparentPower | short | single |  |  |  |  | Apparent power |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 808 | Measurement | Hybrid | ESS | TotalHarmonicDistortion | Hybrid.ESS.TotalHarmonicDistortion | ushort | single |  |  |  |  | Total harmonic distortion |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 32000 | Measurement | Hybrid | ESS | G1Setpoint100kWe | Hybrid.ESS.G1Setpoint100kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 32001 | Measurement | Hybrid | ESS | G1Setpoint80kWe | Hybrid.ESS.G1Setpoint80kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 32002 | Measurement | Hybrid | ESS | G1SetpointEco | Hybrid.ESS.G1SetpointEco | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 0 | Measurement | Genset1 | Generator | Ready | Genset1.Generator.Ready | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 0.1 | Measurement | Genset1 | Generator | Running | Genset1.Generator.Running | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 0.2 | Measurement | Genset1 | Generator | Warning | Genset1.Generator.Warning | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 0.3 | Measurement | Genset1 | Generator | Fault | Genset1.Generator.Fault | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 900 | Measurement | Hybrid | ESS | BargeLoad | Hybrid.ESS.BargeLoad | ushort | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 32003 | Measurement | Hybrid | Ems | G1ControlWord | Hybrid.Ems.G1ControlWord | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 901.15 | Measurement | Hybrid | Ems | Watchdog | Hybrid.Ems.Watchdog | bool | [5 empty] | EMS watchdog to detect network loss |  | TRUE | 3
|  |  |  | 1 | 32004 | Measurement | Hybrid | Ems | G1ShaftLoadPercentage | Hybrid.Ems.G1ShaftLoadPercentage | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 11 | Measurement | Genset1 | Generator | CurrentL1 | Genset1.Generator.CurrentL1 | ushort | single |  | A |  |  | Current L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12 | Measurement | Genset1 | Generator | CurrentL2 | Genset1.Generator.CurrentL2 | ushort | single |  | A |  |  | Current L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 13 | Measurement | Genset1 | Generator | CurrentL3 | Genset1.Generator.CurrentL3 | ushort | single |  | A |  |  | Current L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 14 | Measurement | Genset1 | Generator | VoltageL1L3 | Genset1.Generator.VoltageL1L3 | ushort | single |  | V |  |  | Voltage between L1-L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 15 | Measurement | Genset1 | Generator | VoltageL1L2 | Genset1.Generator.VoltageL1L2 | ushort | single |  | V |  |  | Voltage between L2-L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 16 | Measurement | Genset1 | Generator | VoltageL2L3 | Genset1.Generator.VoltageL2L3 | ushort | single |  | V |  |  | Voltage between L3-L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 17 | Measurement | Genset1 | Generator | VoltageL1N | Genset1.Generator.VoltageL1N | ushort | single |  | V |  |  | Voltage between L1-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 18 | Measurement | Genset1 | Generator | VoltageL2N | Genset1.Generator.VoltageL2N | ushort | single |  | V |  |  | Voltage between L2-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 19 | Measurement | Genset1 | Generator | VoltageL3N | Genset1.Generator.VoltageL3N | ushort | single |  | V |  |  | Voltage between L3-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 20 | Measurement | Genset1 | Generator | FrequencyL1 | Genset1.Generator.FrequencyL1 | ushort | single |  | Hz |  |  | Frequency phase L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 21 | Measurement | Genset1 | Generator | FrequencyL2 | Genset1.Generator.FrequencyL2 | ushort | single |  | Hz |  |  | Frequency phase L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 22 | Measurement | Genset1 | Generator | FrequencyL3 | Genset1.Generator.FrequencyL3 | ushort | single |  | Hz |  |  | Frequency phase L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 23 | Measurement | Genset1 | Generator | ActivePowerL1 | Genset1.Generator.ActivePowerL1 | ushort | single |  | kW |  |  | Active power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 24 | Measurement | Genset1 | Generator | ActivePowerL2 | Genset1.Generator.ActivePowerL2 | ushort | single |  | kW |  |  | Active power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 25 | Measurement | Genset1 | Generator | ActivePowerL3 | Genset1.Generator.ActivePowerL3 | ushort | single |  | kW |  |  | Active power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 26 | Measurement | Genset1 | Generator | ReactivePowerL1 | Genset1.Generator.ReactivePowerL1 | ushort | single |  | kVAr |  |  | Reactive power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 27 | Measurement | Genset1 | Generator | ReactivePowerL2 | Genset1.Generator.ReactivePowerL2 | ushort | single |  | kVAr |  |  | Reactive power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 28 | Measurement | Genset1 | Generator | ReactivePowerL3 | Genset1.Generator.ReactivePowerL3 | ushort | single |  | kVAr |  |  | Reactive power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 29 | Measurement | Genset1 | Generator | ApparentPowerL1 | Genset1.Generator.ApparentPowerL1 | ushort | single |  | kVA |  |  | Apparent power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 30 | Measurement | Genset1 | Generator | ApparentPowerL2 | Genset1.Generator.ApparentPowerL2 | ushort | single |  | kVA |  |  | Apparent power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 31 | Measurement | Genset1 | Generator | ApparentPowerL3 | Genset1.Generator.ApparentPowerL3 | ushort | single |  | kVA |  |  | Apparent power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 32 | Measurement | Genset1 | Generator | PhaseAngleL1 | Genset1.Generator.PhaseAngleL1 | ushort | single |  | ° |  |  | Phase angle L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 33 | Measurement | Genset1 | Generator | PhaseAngleL2 | Genset1.Generator.PhaseAngleL2 | ushort | single |  | ° |  |  | Phase angle L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 34 | Measurement | Genset1 | Generator | PhaseAngleL3 | Genset1.Generator.PhaseAngleL3 | ushort | single |  | ° |  |  | Phase angle L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 35 | Measurement | Genset1 | Generator | CosPhiL1 | Genset1.Generator.CosPhiL1 | ushort | single |  |  |  |  | Cos phi L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 36 | Measurement | Genset1 | Generator | CosPhiL2 | Genset1.Generator.CosPhiL2 | ushort | single |  |  |  |  | Cos phi L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 37 | Measurement | Genset1 | Generator | CosPhiL3 | Genset1.Generator.CosPhiL3 | ushort | single |  |  |  |  | Cos phi L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 38 | Measurement | Genset1 | Generator | PowerFactorL1 | Genset1.Generator.PowerFactorL1 | ushort | single |  |  |  |  | Power factor L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 39 | Measurement | Genset1 | Generator | PowerFactorL2 | Genset1.Generator.PowerFactorL2 | ushort | single |  |  |  |  | Power factor L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 40 | Measurement | Genset1 | Generator | PowerFactorL3 | Genset1.Generator.PowerFactorL3 | ushort | single |  |  |  |  | Power factor L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 101 | Measurement | Genset2 | Generator | Voltage | Genset2.Generator.Voltage | ushort | single |  | V |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 102 | Measurement | Genset2 | Generator | Frequency | Genset2.Generator.Frequency | ushort | single |  | Hz |  |  |  |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 103 | Measurement | Genset2 | Generator | ActivePowerTotal | Genset2.Generator.ActivePowerTotal | short | single |  | kW |  |  |  |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 106 | Measurement | Genset2 | Generator | CosPhi | Genset2.Generator.CosPhi | ushort | single | [6 empty] | TRUE | 3 |  | 0.001 | 3
|  |  |  | 1 | 107 | Measurement | Genset2 | Generator | ApparentPowerTotal | Genset2.Generator.ApparentPowerTotal | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 108 | Measurement | Genset2 | Generator | TotalHarmonicDistortion | Genset2.Generator.TotalHarmonicDistortion | ushort | single | [6 empty] | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 109 | Measurement | Genset2 | Generator | AmbientTemperature | Genset2.Generator.AmbientTemperature | short | single | [6 empty] | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 100 | Measurement | Genset2 | Generator | Ready | Genset2.Generator.Ready | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 100.1 | Measurement | Genset2 | Generator | Running | Genset2.Generator.Running | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 100.2 | Measurement | Genset2 | Generator | Warning | Genset2.Generator.Warning | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 100.3 | Measurement | Genset2 | Generator | Fault | Genset2.Generator.Fault | bool | [7 empty] | TRUE | 3
|  |  |  | 1 | 111 | Measurement | Genset2 | Generator | CurrentL1 | Genset2.Generator.CurrentL1 | ushort | single |  | A |  |  | Current L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 112 | Measurement | Genset2 | Generator | CurrentL2 | Genset2.Generator.CurrentL2 | ushort | single |  | A |  |  | Current L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 113 | Measurement | Genset2 | Generator | CurrentL3 | Genset2.Generator.CurrentL3 | ushort | single |  | A |  |  | Current L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 114 | Measurement | Genset2 | Generator | VoltageL1L3 | Genset2.Generator.VoltageL1L3 | ushort | single |  | V |  |  | Voltage between L1-L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 115 | Measurement | Genset2 | Generator | VoltageL1L2 | Genset2.Generator.VoltageL1L2 | ushort | single |  | V |  |  | Voltage between L2-L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 116 | Measurement | Genset2 | Generator | VoltageL2L3 | Genset2.Generator.VoltageL2L3 | ushort | single |  | V |  |  | Voltage between L3-L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 117 | Measurement | Genset2 | Generator | VoltageL1N | Genset2.Generator.VoltageL1N | ushort | single |  | V |  |  | Voltage between L1-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 118 | Measurement | Genset2 | Generator | VoltageL2N | Genset2.Generator.VoltageL2N | ushort | single |  | V |  |  | Voltage between L2-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 119 | Measurement | Genset2 | Generator | VoltageL3N | Genset2.Generator.VoltageL3N | ushort | single |  | V |  |  | Voltage between L3-N |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 120 | Measurement | Genset2 | Generator | FrequencyL1 | Genset2.Generator.FrequencyL1 | ushort | single |  | Hz |  |  | Frequency phase L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 121 | Measurement | Genset2 | Generator | FrequencyL2 | Genset2.Generator.FrequencyL2 | ushort | single |  | Hz |  |  | Frequency phase L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 122 | Measurement | Genset2 | Generator | FrequencyL3 | Genset2.Generator.FrequencyL3 | ushort | single |  | Hz |  |  | Frequency phase L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 123 | Measurement | Genset2 | Generator | ActivePowerL1 | Genset2.Generator.ActivePowerL1 | ushort | single |  | kW |  |  | Active power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 124 | Measurement | Genset2 | Generator | ActivePowerL2 | Genset2.Generator.ActivePowerL2 | ushort | single |  | kW |  |  | Active power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 125 | Measurement | Genset2 | Generator | ActivePowerL3 | Genset2.Generator.ActivePowerL3 | ushort | single |  | kW |  |  | Active power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 126 | Measurement | Genset2 | Generator | ReactivePowerL1 | Genset2.Generator.ReactivePowerL1 | ushort | single |  | kVAr |  |  | Reactive power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 127 | Measurement | Genset2 | Generator | ReactivePowerL2 | Genset2.Generator.ReactivePowerL2 | ushort | single |  | kVAr |  |  | Reactive power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 128 | Measurement | Genset2 | Generator | ReactivePowerL3 | Genset2.Generator.ReactivePowerL3 | ushort | single |  | kVAr |  |  | Reactive power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 129 | Measurement | Genset2 | Generator | ApparentPowerL1 | Genset2.Generator.ApparentPowerL1 | ushort | single |  | kVA |  |  | Apparent power L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 130 | Measurement | Genset2 | Generator | ApparentPowerL2 | Genset2.Generator.ApparentPowerL2 | ushort | single |  | kVA |  |  | Apparent power L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 131 | Measurement | Genset2 | Generator | ApparentPowerL3 | Genset2.Generator.ApparentPowerL3 | ushort | single |  | kVA |  |  | Apparent power L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 132 | Measurement | Genset2 | Generator | PhaseAngleL1 | Genset2.Generator.PhaseAngleL1 | ushort | single |  | ° |  |  | Phase angle L1 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 133 | Measurement | Genset2 | Generator | PhaseAngleL2 | Genset2.Generator.PhaseAngleL2 | ushort | single |  | ° |  |  | Phase angle L2 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 134 | Measurement | Genset2 | Generator | PhaseAngleL3 | Genset2.Generator.PhaseAngleL3 | ushort | single |  | ° |  |  | Phase angle L3 |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 135 | Measurement | Genset2 | Generator | CosPhiL1 | Genset2.Generator.CosPhiL1 | ushort | single |  |  |  |  | Cos phi L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 136 | Measurement | Genset2 | Generator | CosPhiL2 | Genset2.Generator.CosPhiL2 | ushort | single |  |  |  |  | Cos phi L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 137 | Measurement | Genset2 | Generator | CosPhiL3 | Genset2.Generator.CosPhiL3 | ushort | single |  |  |  |  | Cos phi L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 138 | Measurement | Genset2 | Generator | PowerFactorL1 | Genset2.Generator.PowerFactorL1 | ushort | single |  |  |  |  | Power factor L1 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 139 | Measurement | Genset2 | Generator | PowerFactorL2 | Genset2.Generator.PowerFactorL2 | ushort | single |  |  |  |  | Power factor L2 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 140 | Measurement | Genset2 | Generator | PowerFactorL3 | Genset2.Generator.PowerFactorL3 | ushort | single |  |  |  |  | Power factor L3 |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 32100 | Measurement | Hybrid | ESS | G2Setpoint100kWe | Hybrid.ESS.G2Setpoint100kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 32101 | Measurement | Hybrid | ESS | G2Setpoint80kWe | Hybrid.ESS.G2Setpoint80kWe | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 32102 | Measurement | Hybrid | ESS | G2SetpointEco | Hybrid.ESS.G2SetpointEco | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 32104 | Measurement | Hybrid | Ems | G2ShaftLoadPercentage | Hybrid.Ems.G2ShaftLoadPercentage | ushort | [7 empty] | FALSE | 6
|  |  |  | 1 | 32103 | Measurement | Hybrid | Ems | G2ControlWord | Hybrid.Ems.G2ControlWord | ushort | [7 empty] | FALSE | 6