## ESS modbus
Sheet type |  | Modbus RTU Master |  | Data access list
Sheet name |  | ESS målinger |  | Slaveaddresse | Register address | Register group | System | Sensor | Measurement | Tag | Fieldbus data type | Type | Formatter | Unit | Range high | Range low | Description | Update interval | Historian | Function code | Data length | Scale factor | Decimals
Data port |  | ESS |  | 1 | 12288 | Measurement | Hybrid | ESS | StatusReady | Hybrid.ESS.StatusReady | bool | [5 empty] | ESS is ready to start |  | TRUE | 3
|  |  |  | 1 | 12288.1 | Measurement | Hybrid | ESS | StatusRunning | Hybrid.ESS.StatusRunning | bool | [5 empty] | ESS is running, voltage and frequency at setpoint |  | TRUE | 3
Modbus RTU Master settings |  |  |  | 1 | 12288.2 | Measurement | Hybrid | ESS | StatusWarning | Hybrid.ESS.StatusWarning | bool | [5 empty] | ESS has an active warning, reset not needed |  | TRUE | 3
Protocol mode |  |  | TCP | 1 | 12288.3 | Measurement | Hybrid | ESS | StatusFault | Hybrid.ESS.StatusFault | bool | [5 empty] | ESS has an active fault, reset needed |  | TRUE | 3
Request timeout |  |  | 2000 | 1 | 12288.4 | Measurement | Hybrid | ESS | ReadyToConnect | Hybrid.ESS.ReadyToConnect | bool | [5 empty] | ESS is synchronized to U2, ready to connect |  | TRUE | 3
Request timeout |  |  | 100 | 1 | 12288.15 | Measurement | Hybrid | ESS | WatchDog | Hybrid.ESS.WatchDog | bool | [5 empty] | ESS watchdog to detect network loss |  | TRUE | 3
Slave byte order settings |  |  |  | 1 | 12289 | Measurement | Hybrid | ESS | StateOfCharge | Hybrid.ESS.StateOfCharge | ushort | single |  |  |  |  | State of charge |  | TRUE | 3 |  | 0.1 | 1
Slave no. | 16 bit | 32 bit | String | 1 | 12290 | Measurement | Hybrid | ESS | AvailablePower | Hybrid.ESS.AvailablePower | ushort | [5 empty] | Available power |  | TRUE | 3 |  | 0.1 | 1
1 | Modbus | Modbus | Modbus | 1 | 12291 | Measurement | Hybrid | ESS | AvailableEnergy | Hybrid.ESS.AvailableEnergy | ushort | [5 empty] | Available energy |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12292 | Measurement | Hybrid | ESS | EffectiveTimeRem | Hybrid.ESS.EffectiveTimeRem | ushort | [5 empty] | EffectiveTimeRem |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12293 | Measurement | Hybrid | ESS | StateOfHealth | Hybrid.ESS.StateOfHealth | ushort | single |  |  |  |  | ESS state of health |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12294 | Measurement | Hybrid | ESS | GridVoltage | Hybrid.ESS.GridVoltage | ushort | single |  |  |  |  | Grid AC voltage measured at drive side |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12295 | Measurement | Hybrid | ESS | GridFrequency | Hybrid.ESS.GridFrequency | ushort | single |  |  |  |  | Grid frequency measured at drive side |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12296 | Measurement | Hybrid | ESS | DriveActivePower | Hybrid.ESS.DriveActivePower | short | single |  |  |  |  | Drive active power |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12297 | Measurement | Hybrid | ESS | DriveCurrent | Hybrid.ESS.DriveCurrent | short | single |  | A |  |  | Drive AC current |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12298 | Measurement | Hybrid | ESS | BusVoltage | Hybrid.ESS.BusVoltage | ushort | single |  | V |  |  | DC Bus Voltage |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12299 | Measurement | Hybrid | ESS | BusCurrent | Hybrid.ESS.BusCurrent | short | single |  | A |  |  | DC Bus current |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12300 | Measurement | Hybrid | ESS | MaxCellVoltage | Hybrid.ESS.MaxCellVoltage | ushort |  |  | mV |  |  | Maximum cell voltage |  | TRUE | 3
|  |  |  | 1 | 12301 | Measurement | Hybrid | ESS | MinCellVoltage | Hybrid.ESS.MinCellVoltage | ushort |  |  | mV |  |  | Minimum cell voltage |  | TRUE | 3
|  |  |  | 1 | 12302 | Measurement | Hybrid | ESS | AverageCellVoltage | Hybrid.ESS.AverageCellVoltage | ushort |  |  | mV |  |  | Average cell voltage |  | TRUE | 3
|  |  |  | 1 | 12303 | Measurement | Hybrid | ESS | MaxCellTemperature | Hybrid.ESS.MaxCellTemperature | short | [5 empty] | Maximum cell temperature |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12304 | Measurement | Hybrid | ESS | MinCellTemperature | Hybrid.ESS.MinCellTemperature | short | [5 empty] | Minimum cell temperature |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12305 | Measurement | Hybrid | ESS | AverageCellTemperature | Hybrid.ESS.AverageCellTemperature | short | [5 empty] | Average cell temperature |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12306 | Measurement | Hybrid | ESS | DriveReactivePower | Hybrid.ESS.DriveReactivePower | short | [5 empty] | Drive reactive power |  | TRUE | 3 |  | 0.001 | 1
|  |  |  | 1 | 12307 | Measurement | Hybrid | ESS | TransformerAverageCellTemperature | Hybrid.ESS.TransformerAverageCellTemperature | short | [5 empty] | Average of 3 temperature sensor on the transformer |  | TRUE | 3
|  |  |  | 1 | 12308 | Measurement | Hybrid | ESS | WarningWord1 | Hybrid.ESS.WarningWord1 | ushort | [5 empty] | Warning word 1 for battery system |  | TRUE | 3
|  |  |  | 1 | 12309 | Measurement | Hybrid | ESS | WarningWord2 | Hybrid.ESS.WarningWord2 | ushort | [5 empty] | Warning word 2 for battery system |  | TRUE | 3
|  |  |  | 1 | 12310 | Measurement | Hybrid | ESS | FaultWord1 | Hybrid.ESS.FaultWord1 | ushort | [5 empty] | Fault word 1 for battery system |  | TRUE | 3
|  |  |  | 1 | 12311 | Measurement | Hybrid | ESS | FaultWord2 | Hybrid.ESS.FaultWord2 | ushort | [5 empty] | Fault word 2 for battery system |  | TRUE | 3
|  |  |  | 1 | 12312 | Measurement | Hybrid | ESS | ShutdownWord1 | Hybrid.ESS.ShutdownWord1 | ushort | [5 empty] | Shutdown word 1 for battery system |  | TRUE | 3
|  |  |  | 1 | 12313 | Measurement | Hybrid | ESS | ShutdownWord2 | Hybrid.ESS.ShutdownWord2 | ushort | [5 empty] | Shutdown word 2 for battery system |  | TRUE | 3
|  |  |  | 1 | 12314 | Measurement | Hybrid | ESS | PowerFactor | Hybrid.ESS.PowerFactor | ushort | single |  |  |  |  | Power factor for drive |  | TRUE | 3 |  | 0.01 | 2
|  |  |  | 1 | 12315 | Measurement | Hybrid | ESS | MaxAllowedChargePower | Hybrid.ESS.MaxAllowedChargePower | ushort | single |  |  |  |  | Maximum allowed charge power |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12316 | Measurement | Hybrid | ESS | MaxAllowedDischargePower | Hybrid.ESS.MaxAllowedDischargePower | ushort | single |  |  |  |  | Maximum allowed discharge power |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12317 | Measurement | Hybrid | ESS | LowCriticalVoltageIslandMode | Hybrid.ESS.LowCriticalVoltageIslandMode | ushort |  |  | mV |  |  | Low critical voltage battery cells (mV) |  | TRUE | 3
|  |  |  | 1 | 12318 | Parameter | Hybrid | ESS | Battery_kWh | Hybrid.ESS.Battery_kWh | ushort |  |  | kWh |  |  | Battery nominall capacity |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12319 | Measurement | Hybrid | ESS | EffectiveSoC | Hybrid.ESS.EffectiveSoC | ushort | single |  |  |  |  | EffectiveSoC |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12320 | Measurement | Hybrid | ESS | Spare3 | Hybrid.ESS.Spare3 | ushort | [5 empty] | Spare2 |  | TRUE | 3
|  |  |  | 1 | 12321 | Measurement | Hybrid | ESS | RoomTemp | Hybrid.ESS.RoomTemp | ushort | [5 empty] | Ambient temperature battery room |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12322 | Measurement | Hybrid | ESS | Spare4 | Hybrid.ESS.Spare4 | ushort | [5 empty] | Spare3 |  | TRUE | 3
|  |  |  | 1 | 12323 | Measurement | Hybrid | ESS | ESS_Warning | Hybrid.ESS.ESS_Warning | ushort | [5 empty] | ESS_Warning |  | TRUE | 3
|  |  |  | 1 | 12324 | Measurement | Hybrid | ESS | ESS_Warning2 | Hybrid.ESS.ESS_Warning2 | ushort | [5 empty] | ESS_Warning2 |  | TRUE | 3
|  |  |  | 1 | 12325 | Measurement | Hybrid | ESS | ESS_Fault | Hybrid.ESS.ESS_Fault | ushort | [5 empty] | ESS_Fault |  | TRUE | 3
|  |  |  | 1 | 12326 | Measurement | Hybrid | ESS | ESS_Fault2 | Hybrid.ESS.ESS_Fault2 | ushort | [5 empty] | ESS_Fault2 |  | TRUE | 3
|  |  |  | 1 | 12327 | Measurement | Hybrid | ESS | ESS_Shutdown | Hybrid.ESS.ESS_Shutdown | ushort | [5 empty] | ESS_Shutdown |  | TRUE | 3
|  |  |  | 1 | 12328 | Measurement | Hybrid | ESS | ESS_Shutdown2 | Hybrid.ESS.ESS_Shutdown2 | ushort | [5 empty] | ESS_Shutdown2 |  | TRUE | 3
|  |  |  | 1 | 12329 | Measurement | Hybrid | ESS | Spare5 | Hybrid.ESS.Spare5 | ushort | [5 empty] | Spare5 |  | TRUE | 3
|  |  |  | 1 | 12330 | Measurement | Hybrid | ESS | TimeRemaining | Hybrid.ESS.TimeRemaining | ushort | [5 empty] | Time remaining |  | TRUE | 3
|  |  |  | 1 | 12331 | Measurement | Hybrid | ESS | TripSoC | Hybrid.ESS.TripSoC | ushort | single |  |  |  |  | TripSoC |  | TRUE | 3 |  | 0.1 | 1
|  |  |  | 1 | 12332 | Measurement | Hybrid | ESS | TripTime | Hybrid.ESS.TripTime | ushort | [5 empty] | TripTime |  | TRUE | 3
|  |  |  | 1 | 12333 | Measurement | Hybrid | ESS | Spare 45 | Hybrid.ESS.Spare 45 | ushort | [5 empty] | Spare 45 |  | TRUE | 3
|  |  |  | 1 | 12334 | Measurement | Hybrid | ESS | Spare 46 | Hybrid.ESS.Spare 46 | ushort | [5 empty] | Spare 46 |  | TRUE | 3
|  |  |  | 1 | 12335 | Measurement | Hybrid | ESS | Spare 47 | Hybrid.ESS.Spare 47 | ushort | [5 empty] | Spare 47 |  | TRUE | 3
|  |  |  | 1 | 12336 | Measurement | Hybrid | ESS | Spare 48 | Hybrid.ESS.Spare 48 | ushort | [5 empty] | Spare 48 |  | TRUE | 3
|  |  |  | 1 | 12337 | Measurement | Hybrid | ESS | Spare 49 | Hybrid.ESS.Spare 49 | ushort | [5 empty] | Spare 49 |  | TRUE | 3
|  |  |  | 1 | 12338 | Parameter | a | ESS | PLC_SW_Version | a.ESS.PLC_SW_Version | ushort | [5 empty] | PLC_SW_Version |  | TRUE | 3
|  |  |  | 1 | 12339 | Parameter | a | ESS | HMI_SW_Version | a.ESS.HMI_SW_Version | ushort | [5 empty] | HMI_SW_Version |  | TRUE | 3