## Generator
Sheet type |  | Modbus RTU Master |  | Data access list
Sheet name |  | Generatormålinger |  | Slaveaddresse | Register address | Register group | System | Sensor | Measurement | Tag | Fieldbus data type | Type | Formatter | Unit | Range high | Range low | Description | Update interval | Historian | Function code | Data length | Scale factor | Decimals
Data port |  |  |  |  | 0 | Measurement | Genset1 | Mains | VoltageL1L2 | Genset1.Mains.VoltageL1L2 |  | single | Sices_UL_08 | Vac |  |  | Mains/busbars: voltage L1-L2 |  | TRUE | 4
[5 empty] | 2 | Measurement | Genset1 | Mains | VoltageL2L3 | Genset1.Mains.VoltageL2L3 |  | single | Sices_UL_08 | Vac |  |  | Mains/busbars: voltage L2-L3 |  | TRUE | 4
Modbus RTU Master settings |  |  |  |  | 4 | Measurement | Genset1 | Mains | VoltageL1L3 | Genset1.Mains.VoltageL1L3 |  | single | Sices_UL_08 | Vac |  |  | Mains/busbars: voltage L3-L1 |  | TRUE | 4
Protocol mode |  |  |  |  | 29 | Measurement | Genset1 | Mains | Frequency | Genset1.Mains.Frequency | ushort | single | Sices_US_08 | Hz |  |  |  |  | TRUE | 4
Request timeout |  |  |  |  | 6 | Measurement | Genset1 | Generator | VoltageL1L2 | Genset1.Generator.VoltageL1L2 |  | single | Sices_UL_08 | Vac |  |  |  |  | TRUE | 4
[5 empty] | 8 | Measurement | Genset1 | Generator | VoltageL2L3 | Genset1.Generator.VoltageL2L3 |  | single | Sices_UL_08 | Vac |  |  |  |  | TRUE | 4
Slave byte order settings |  |  |  |  | 10 | Measurement | Genset1 | Generator | VoltageL1L3 | Genset1.Generator.VoltageL1L3 |  | single | Sices_UL_08 | Vac |  |  |  |  | TRUE | 4
Slave no. | 16 bit | 32 bit | String |  | 28 | Measurement | Genset1 | Generator | Frequency | Genset1.Generator.Frequency | ushort | single | Sices_US_08 | Hz |  |  |  |  | TRUE | 4
| Modbus | Modbus | Modbus |  | 20 | Measurement | Genset1 | Generator | CurrentL1 | Genset1.Generator.CurrentL1 |  | single | Sices_UL_08 | Aac |  |  |  |  | TRUE | 4
[5 empty] | 22 | Measurement | Genset1 | Generator | CurrentL2 | Genset1.Generator.CurrentL2 |  | single | Sices_UL_08 | Aac |  |  |  |  | TRUE | 4
[5 empty] | 24 | Measurement | Genset1 | Generator | CurrentL3 | Genset1.Generator.CurrentL3 |  | single | Sices_UL_08 | Aac |  |  |  |  | TRUE | 4
[5 empty] | 30 | Measurement | Genset1 | Generator | ActivePowerL1 | Genset1.Generator.ActivePowerL1 |  | single | Sices_SL_08 | kW |  |  |  |  | TRUE | 4
[5 empty] | 40 | Measurement | Genset1 | Generator | ActivePowerL2 | Genset1.Generator.ActivePowerL2 |  | single | Sices_SL_08 | kW |  |  |  |  | TRUE | 4
[5 empty] | 50 | Measurement | Genset1 | Generator | ActivePowerL3 | Genset1.Generator.ActivePowerL3 |  | single | Sices_SL_08 | kW |  |  |  |  | TRUE | 4
[5 empty] | 60 | Measurement | Genset1 | Generator | ActivePowerTotal | Genset1.Generator.ActivePowerTotal |  | single | Sices_SL_08 | kW |  |  |  |  | TRUE | 4
[5 empty] | 32 | Measurement | Genset1 | Generator | ReactivePowerL1 | Genset1.Generator.ReactivePowerL1 |  | single | Sices_SL_08 | kVAr |  |  |  |  | TRUE | 4
[5 empty] | 42 | Measurement | Genset1 | Generator | ReactivePowerL2 | Genset1.Generator.ReactivePowerL2 |  | single | Sices_SL_08 | kVAr |  |  |  |  | TRUE | 4
[5 empty] | 52 | Measurement | Genset1 | Generator | ReactivePowerL3 | Genset1.Generator.ReactivePowerL3 |  | single | Sices_SL_08 | kVAr |  |  |  |  | TRUE | 4
[5 empty] | 62 | Measurement | Genset1 | Generator | ReactivePowerTotal | Genset1.Generator.ReactivePowerTotal |  | single | Sices_SL_08 | kVAr |  |  |  |  | TRUE | 4
[5 empty] | 34 | Measurement | Genset1 | Generator | ApparentPowerL1 | Genset1.Generator.ApparentPowerL1 |  | single | Sices_UL_08 | kVA |  |  |  |  | TRUE | 4
[5 empty] | 44 | Measurement | Genset1 | Generator | ApparentPowerL2 | Genset1.Generator.ApparentPowerL2 |  | single | Sices_UL_08 | kVA |  |  |  |  | TRUE | 4
[5 empty] | 54 | Measurement | Genset1 | Generator | ApparentPowerL3 | Genset1.Generator.ApparentPowerL3 |  | single | Sices_UL_08 | kVA |  |  |  |  | TRUE | 4
[5 empty] | 64 | Measurement | Genset1 | Generator | ApparentPowerTotal | Genset1.Generator.ApparentPowerTotal |  | single | Sices_UL_08 | kVA |  |  |  |  | TRUE | 4
[5 empty] | 67 | Measurement | Genset1 | Generator | CosPhi | Genset1.Generator.CosPhi | ushort | single | Sices_SS_08 | [5 empty] | TRUE | 4
[5 empty] | 131 | Measurement | Genset1 | Engine | StatusString | Genset1.Engine.StatusString |  | ushort | [6 empty] | TRUE | 4
[5 empty] | 188 | Measurement | Genset1 | Engine | OilPressure | Genset1.Engine.OilPressure | ushort | single | Sices_US_08 | bar |  |  |  |  | TRUE | 4
[5 empty] | 77 | Measurement | Genset1 | Engine | CoolantTemperature | Genset1.Engine.CoolantTemperature |  | single | Sices_SL_08 | deg. C |  |  |  |  | TRUE | 4
[5 empty] | 126 | Measurement | Genset1 | Generator | VoltageStatusL1L2 | Genset1.Generator.VoltageStatusL1L2 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 127 | Measurement | Genset1 | Generator | VoltageStatusL2L3 | Genset1.Generator.VoltageStatusL2L3 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 128 | Measurement | Genset1 | Generator | VoltageStatusL1L3 | Genset1.Generator.VoltageStatusL1L3 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 121 | Measurement | Genset1 | Mains | VoltageStatusL1L2 | Genset1.Mains.VoltageStatusL1L2 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 122 | Measurement | Genset1 | Mains | VoltageStatusL2L3 | Genset1.Mains.VoltageStatusL2L3 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 123 | Measurement | Genset1 | Mains | VoltageStatusL1L3 | Genset1.Mains.VoltageStatusL1L3 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 144 | Measurement | Genset1 | Mains | FrequencyStatus | Genset1.Mains.FrequencyStatus |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 129 | Measurement | Genset1 | Generator | FrequencyStatus | Genset1.Generator.FrequencyStatus |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 304 | Parameter | Genset1 | Generator | NumberOfPhases | Genset1.Generator.NumberOfPhases |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 305 | Parameter | Genset1 | Generator | NominalVoltage | Genset1.Generator.NominalVoltage |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 306 | Parameter | Genset1 | Generator | VTPrimaryVoltage | Genset1.Generator.VTPrimaryVoltage |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 307 | Parameter | Genset1 | Generator | VTSecondaryVoltage | Genset1.Generator.VTSecondaryVoltage |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 308 | Parameter | Genset1 | Generator | NominalFrequency | Genset1.Generator.NominalFrequency |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 309 | Parameter | Genset1 | Generator | NominalPower | Genset1.Generator.NominalPower |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 310 | Parameter | Genset1 | Generator | LoadCTRatio | Genset1.Generator.LoadCTRatio |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 311 | Parameter | Genset1 | Generator | AuxCurrentRatio | Genset1.Generator.AuxCurrentRatio |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 312 | Parameter | Genset1 | Generator | AuxCurrentFunction | Genset1.Generator.AuxCurrentFunction |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 313 | Parameter | Genset1 | Engine | PickupWheelTeethCount | Genset1.Engine.PickupWheelTeethCount |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 314 | Parameter | Genset1 | Engine | Wratio | Genset1.Engine.Wratio | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 315 | Parameter | Genset1 | Engine | OilPressureSensorType | Genset1.Engine.OilPressureSensorType |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 316 | Parameter | Genset1 | Engine | CoolantTemperatureSensorType | Genset1.Engine.CoolantTemperatureSensorType |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 317 | Parameter | Genset1 | Engine | FuelLevelSensorType | Genset1.Engine.FuelLevelSensorType |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 318 | Parameter | Genset1 | Engine | DInputFunction | Genset1.Engine.DInputFunction |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 319 | Parameter | Genset1 | Mains | NominalVoltage | Genset1.Mains.NominalVoltage |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 320 | Parameter | Genset1 | Mains | VTPrimaryVoltage | Genset1.Mains.VTPrimaryVoltage |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 321 | Parameter | Genset1 | Mains | VTSecondaryVoltage | Genset1.Mains.VTSecondaryVoltage |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 483 | Parameter | Genset1 | Mains | NumberOfPhases | Genset1.Mains.NumberOfPhases |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 575 | Parameter | Genset1 | Mains | CTConnections | Genset1.Mains.CTConnections |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 548 | Parameter | Genset1 | Engine | NominalPower | Genset1.Engine.NominalPower |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1822 | Parameter | Genset1 | Engine | RPMFrequencyRatio | Genset1.Engine.RPMFrequencyRatio |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1979 | Parameter | Genset1 | Generator | CTSecondaryAux | Genset1.Generator.CTSecondaryAux |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1978 | Parameter | Genset1 | Generator | CTSecondary | Genset1.Generator.CTSecondary |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1831 | Parameter | Genset1 | Generator | DITELModuleCount | Genset1.Generator.DITELModuleCount |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1832 | Parameter | Genset1 | Generator | DIGRINModuleCount | Genset1.Generator.DIGRINModuleCount |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1833 | Parameter | Genset1 | Generator | DIVITModuleCount | Genset1.Generator.DIVITModuleCount |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1834 | Parameter | Genset1 | Generator | DANOUTModuleCount | Genset1.Generator.DANOUTModuleCount |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 544 | Parameter | Genset1 | Generator | VoltageInputType | Genset1.Generator.VoltageInputType |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 579 | Parameter | Genset1 | Mains | VoltageInputType | Genset1.Mains.VoltageInputType |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 322 | Parameter | Genset1 | Mains | VoltageHysteresis | Genset1.Mains.VoltageHysteresis | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 323 | Parameter | Genset1 | Generator | VoltageHysteresis | Genset1.Generator.VoltageHysteresis | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 324 | Parameter | Genset1 | Mains | LowVoltageThreshold | Genset1.Mains.LowVoltageThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 325 | Parameter | Genset1 | Mains | HighVoltageThreshold | Genset1.Mains.HighVoltageThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 326 | Parameter | Genset1 | Mains | PresenceDelay | Genset1.Mains.PresenceDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 327 | Parameter | Genset1 | Mains | FaultDelay | Genset1.Mains.FaultDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 328 | Parameter | Genset1 | Mains | InhibitionActivationDelay | Genset1.Mains.InhibitionActivationDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 329 | Parameter | Genset1 | Mains | InhibitionDeactivationDelay | Genset1.Mains.InhibitionDeactivationDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 330 | Parameter | Genset1 | Engine | PreheatCycleDuration | Genset1.Engine.PreheatCycleDuration |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 331 | Parameter | Genset1 | Engine | StarterPulseDuration | Genset1.Engine.StarterPulseDuration |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 332 | Parameter | Genset1 | Engine | NumberOfCrankAttempts | Genset1.Engine.NumberOfCrankAttempts |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 333 | Parameter | Genset1 | Engine | TimeBetweenCrankAttempts | Genset1.Engine.TimeBetweenCrankAttempts |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 334 | Parameter | Genset1 | Engine | StopPulseDuration | Genset1.Engine.StopPulseDuration |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 335 | Parameter | Genset1 | Engine | StopCycleDuration | Genset1.Engine.StopCycleDuration |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 336 | Parameter | Genset1 | Engine | CoolingCycleDuration | Genset1.Engine.CoolingCycleDuration |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 337 | Parameter | Genset1 | Engine | EngineProtectionMaskTime | Genset1.Engine.EngineProtectionMaskTime |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 338 | Parameter | Genset1 | Engine | OperatingConditionsMaxTime | Genset1.Engine.OperatingConditionsMaxTime |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 339 | Parameter | Genset1 | Mains | DelayBeforeSupply | Genset1.Mains.DelayBeforeSupply |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 340 | Parameter | Genset1 | Mains | ContactorsSwapDelay | Genset1.Mains.ContactorsSwapDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 341 | Parameter | Genset1 | Mains | ContactorsHoldingTime | Genset1.Mains.ContactorsHoldingTime |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 342 | Parameter | Genset1 | Generator | EnableSupplyOnMCBFault | Genset1.Generator.EnableSupplyOnMCBFault |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 343 | Parameter | Genset1 | Generator | EnableSupplyOnTest | Genset1.Generator.EnableSupplyOnTest |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 344 | Parameter | Genset1 | Engine | MinRatedCoolantTemperature | Genset1.Engine.MinRatedCoolantTemperature |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 345 | Parameter | Genset1 | Engine | StoppedThresholdRPM | Genset1.Engine.StoppedThresholdRPM | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 346 | Parameter | Genset1 | Engine | RunningThresholdRPM | Genset1.Engine.RunningThresholdRPM | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 347 | Parameter | Genset1 | Engine | StoppedThresholdVoltage | Genset1.Engine.StoppedThresholdVoltage | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 348 | Parameter | Genset1 | Engine | RunningThresholdVoltage | Genset1.Engine.RunningThresholdVoltage | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 349 | Parameter | Genset1 | Engine | StoppedThresholdFrequency | Genset1.Engine.StoppedThresholdFrequency | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 350 | Parameter | Genset1 | Engine | RunningThresholdFrequency | Genset1.Engine.RunningThresholdFrequency | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 491 | Parameter | Genset1 | Engine | IdleSpeedDuration | Genset1.Engine.IdleSpeedDuration |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 545 | Parameter | Genset1 | Engine | FuelSolenoidClosureDelay | Genset1.Engine.FuelSolenoidClosureDelay | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 1816 | Parameter | Genset1 | Mains | LowFrequencyThreshold | Genset1.Mains.LowFrequencyThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 1817 | Parameter | Genset1 | Mains | HighFrequencyThreshold | Genset1.Mains.HighFrequencyThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 1818 | Parameter | Genset1 | Mains | VoltageunbalanceThreshold | Genset1.Mains.VoltageunbalanceThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 1819 | Parameter | Genset1 | Mains | RequiredPhaseSequence | Genset1.Mains.RequiredPhaseSequence |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 353 | Parameter | Genset1 | Generator | MinVoltageThreshold | Genset1.Generator.MinVoltageThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 354 | Parameter | Genset1 | Generator | MinVoltageDelay | Genset1.Generator.MinVoltageDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 355 | Parameter | Genset1 | Generator | MaxVoltageThreshold | Genset1.Generator.MaxVoltageThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 356 | Parameter | Genset1 | Generator | MaxVoltageDelay | Genset1.Generator.MaxVoltageDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 357 | Parameter | Genset1 | Generator | MinFrequencyThreshold | Genset1.Generator.MinFrequencyThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 358 | Parameter | Genset1 | Generator | MinFrequencyDelay | Genset1.Generator.MinFrequencyDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 359 | Parameter | Genset1 | Generator | MaxFrequencyThreshold | Genset1.Generator.MaxFrequencyThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 360 | Parameter | Genset1 | Generator | MaxFrequencyDelay | Genset1.Generator.MaxFrequencyDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 361 | Parameter | Genset1 | Generator | MaxCurrentThreshold | Genset1.Generator.MaxCurrentThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 362 | Parameter | Genset1 | Generator | MaxCurrentDelay | Genset1.Generator.MaxCurrentDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 363 | Parameter | Genset1 | Generator | ShortCircuitThreshold | Genset1.Generator.ShortCircuitThreshold |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 364 | Parameter | Genset1 | Generator | ShortCircuitDelay | Genset1.Generator.ShortCircuitDelay | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 365 | Parameter | Genset1 | Generator | PowerReverseThreshold | Genset1.Generator.PowerReverseThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 366 | Parameter | Genset1 | Generator | PowerReverseDelay | Genset1.Generator.PowerReverseDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 471 | Parameter | Genset1 | Generator | VoltageunbalanceThreshold | Genset1.Generator.VoltageunbalanceThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 472 | Parameter | Genset1 | Generator | VoltageunbalanceDelay | Genset1.Generator.VoltageunbalanceDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 473 | Parameter | Genset1 | Generator | CurrentUnbalanceThreshold | Genset1.Generator.CurrentUnbalanceThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 474 | Parameter | Genset1 | Generator | CurrentUnbalanceDelay | Genset1.Generator.CurrentUnbalanceDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 484 | Parameter | Genset1 | Generator | RequiredPhaseSequence | Genset1.Generator.RequiredPhaseSequence |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 492 | Parameter | Genset1 | Generator | LossOfExitationThreshold | Genset1.Generator.LossOfExitationThreshold |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 493 | Parameter | Genset1 | Generator | LossOfExitationDelay | Genset1.Generator.LossOfExitationDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 367 | Parameter | Genset1 | Engine | FrequencyOverspeedThreshold | Genset1.Engine.FrequencyOverspeedThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 368 | Parameter | Genset1 | Engine | FrequencyOverspeedDelay | Genset1.Engine.FrequencyOverspeedDelay | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 369 | Parameter | Genset1 | Engine | PickupOverspeedThreshold | Genset1.Engine.PickupOverspeedThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 370 | Parameter | Genset1 | Engine | PickupOverspeedDelay | Genset1.Engine.PickupOverspeedDelay | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 371 | Parameter | Genset1 | Engine | HighCoolantTemperatureThreshold | Genset1.Engine.HighCoolantTemperatureThreshold |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 372 | Parameter | Genset1 | Engine | HighCoolantTemperatureDelay | Genset1.Engine.HighCoolantTemperatureDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 373 | Parameter | Genset1 | Engine | MaxCoolantTemperatureThreshold | Genset1.Engine.MaxCoolantTemperatureThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 374 | Parameter | Genset1 | Engine | MaxCoolantTemperatureDelay | Genset1.Engine.MaxCoolantTemperatureDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 375 | Parameter | Genset1 | Engine | LowOilpressureThreshold | Genset1.Engine.LowOilpressureThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 376 | Parameter | Genset1 | Engine | LowOilPressureDelay | Genset1.Engine.LowOilPressureDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 377 | Parameter | Genset1 | Engine | MinOilPressureThreshold | Genset1.Engine.MinOilPressureThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 378 | Parameter | Genset1 | Engine | MinOilPressureDelay | Genset1.Engine.MinOilPressureDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 379 | Parameter | Genset1 | Engine | HighFuelLevelThreshold | Genset1.Engine.HighFuelLevelThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 380 | Parameter | Genset1 | Engine | HighFuelLevelDelay | Genset1.Engine.HighFuelLevelDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 381 | Parameter | Genset1 | Engine | LowFuelLevelThreshold | Genset1.Engine.LowFuelLevelThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 382 | Parameter | Genset1 | Engine | LowFuelLevelDelay | Genset1.Engine.LowFuelLevelDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 383 | Parameter | Genset1 | Engine | MinFuelLevelThreshold | Genset1.Engine.MinFuelLevelThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 384 | Parameter | Genset1 | Engine | MinFuelLevelDelay | Genset1.Engine.MinFuelLevelDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 385 | Parameter | Genset1 | Engine | BeltBreakDelay | Genset1.Engine.BeltBreakDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 529 | Parameter | Genset1 | Engine | MaxPowerThreshold | Genset1.Engine.MaxPowerThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 530 | Parameter | Genset1 | Engine | MaxPowerDelay | Genset1.Engine.MaxPowerDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 538 | Parameter | Genset1 | Engine | LowCoolantTemperatureThreshold | Genset1.Engine.LowCoolantTemperatureThreshold |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 539 | Parameter | Genset1 | Engine | LowCoolantTemperatureDelay | Genset1.Engine.LowCoolantTemperatureDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 1974 | Parameter | Genset1 | Engine | MinSpeedThreshold | Genset1.Engine.MinSpeedThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 1975 | Parameter | Genset1 | Engine | MinSpeedDelay | Genset1.Engine.MinSpeedDelay | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 387 | Parameter | Genset1 | Engine | LowBatteryVoltageThreshold | Genset1.Engine.LowBatteryVoltageThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 388 | Parameter | Genset1 | Engine | LowBatteryVoltagelDelay | Genset1.Engine.LowBatteryVoltagelDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 389 | Parameter | Genset1 | Engine | HighBatteryVoltageThreshold | Genset1.Engine.HighBatteryVoltageThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 390 | Parameter | Genset1 | Engine | HighBatteryVoltageDelay | Genset1.Engine.HighBatteryVoltageDelay |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 391 | Parameter | Genset1 | Engine | HighBoardTemperatureThreshold | Genset1.Engine.HighBoardTemperatureThreshold | ushort | single | Sices_US_08 | [5 empty] | FALSE | 3
[5 empty] | 546 | Parameter | Genset1 | Engine | FuelPumpMode | Genset1.Engine.FuelPumpMode |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 392 | Parameter | Genset1 | Engine | FuelpumpSensorType | Genset1.Engine.FuelpumpSensorType |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 393 | Parameter | Genset1 | Engine | FuelPumpStartThreshold | Genset1.Engine.FuelPumpStartThreshold |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 394 | Parameter | Genset1 | Engine | FuelPumpStopThreshold | Genset1.Engine.FuelPumpStopThreshold |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 800 | Measurement | Genset1 | Engine | Alarms1 | Genset1.Engine.Alarms1 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 801 | Measurement | Genset1 | Engine | Alarms2 | Genset1.Engine.Alarms2 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 136 | Measurement | Genset1 | Engine | ManagementFlag | Genset1.Engine.ManagementFlag |  | ushort | [6 empty] | TRUE | 4
[5 empty] | 142 | Measurement | Genset1 | Engine | StatusOfSpeed | Genset1.Engine.StatusOfSpeed |  | ushort | [6 empty] | TRUE | 4
[5 empty] | 73 | Measurement | Genset1 | Engine | BatteryVoltage | Genset1.Engine.BatteryVoltage | ushort | single | Sices_US_08 | [5 empty] | TRUE | 4
[5 empty] | 802 | Measurement | Genset1 | Engine | Alarms3 | Genset1.Engine.Alarms3 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 803 | Measurement | Genset1 | Engine | Alarms4 | Genset1.Engine.Alarms4 |  | ushort | [6 empty] | FALSE | 4
[5 empty] | 107 | Parameter | Genset1 | Generator | ControllerSerialNo | Genset1.Generator.ControllerSerialNo |  | string | Sices_SHEX3 | [5 empty] | TRUE | 4 | 6
[5 empty] | 120 | Measurement | Genset1 | Generator | OperatingMode | Genset1.Generator.OperatingMode |  | ushort | [6 empty] | TRUE | 4
[5 empty] | 132 | Measurement | Genset1 | Generator | SequenceState | Genset1.Generator.SequenceState |  | ushort | [6 empty] | TRUE | 4
[5 empty] | 71 | Measurement | Genset1 | Engine | RunningHours | Genset1.Engine.RunningHours | uint | single | [6 empty] | TRUE | 4