## Generator
Sheet type |  | Modbus RTU Master |  | Data access list
Sheet name |  | Generatormålinger |  | Slaveaddresse | Register address | Register group | System | Sensor | Measurement | Tag | Fieldbus data type | Type | Formatter | Unit | Range high | Range low | Description | Update interval | Historian | Function code | Data length | Scale factor | Decimals
Data port |  |  |  |  | 1024 | Measurement | Genset1 | Engine | OilPressure | Genset1.Engine.OilPressure | ushort |  |  | bar |  |  | Engine oil pressure |  | TRUE | 3 |  | 0.01 | 2
[5 empty] | 1025 | Measurement | Genset1 | Engine | CoolantTemperature | Genset1.Engine.CoolantTemperature |  | short |  | °C |  |  | Engine coolant temperature |  | TRUE | 3
Modbus RTU Master settings |  |  |  |  | 1029 | Measurement | Genset1 | Engine | BatteryVoltage | Genset1.Engine.BatteryVoltage | ushort |  |  | V |  |  | Engine battery voltage |  | TRUE | 3 |  | 0.1 | 0
Protocol mode |  |  |  |  | 1030 | Measurement | Genset1 | Engine | EngineSpeed | Genset1.Engine.EngineSpeed |  | ushort |  | RPM |  |  | Engine RPM |  | TRUE | 3
Request timeout |  |  |  |  | 1798 | Measurement | Genset1 | Engine | RunningHours | Genset1.Engine.RunningHours | uint |  |  | h |  |  | Engine total running hours |  | TRUE | 3 |  | 0.00027778 | 2
[5 empty] | 39425 | Measurement | Genset1 | Alarms | Word1 | Genset1.Alarms.Word1 |  | ushort | [6 empty] | FALSE | 3
Slave byte order settings |  |  |  |  | 39426 | Measurement | Genset1 | Alarms | Word2 | Genset1.Alarms.Word2 |  | ushort | [6 empty] | FALSE | 3
Slave no. | 16 bit | 32 bit | String |  | 39427 | Measurement | Genset1 | Alarms | Word3 | Genset1.Alarms.Word3 |  | ushort | [6 empty] | FALSE | 3
| Modbus | Modbus | Modbus |  | 39428 | Measurement | Genset1 | Alarms | Word4 | Genset1.Alarms.Word4 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39429 | Measurement | Genset1 | Alarms | Word5 | Genset1.Alarms.Word5 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39430 | Measurement | Genset1 | Alarms | Word6 | Genset1.Alarms.Word6 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39431 | Measurement | Genset1 | Alarms | Word7 | Genset1.Alarms.Word7 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39432 | Measurement | Genset1 | Alarms | Word8 | Genset1.Alarms.Word8 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39433 | Measurement | Genset1 | Alarms | Word9 | Genset1.Alarms.Word9 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39434 | Measurement | Genset1 | Alarms | Word10 | Genset1.Alarms.Word10 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39435 | Measurement | Genset1 | Alarms | Word11 | Genset1.Alarms.Word11 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39436 | Measurement | Genset1 | Alarms | Word12 | Genset1.Alarms.Word12 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39437 | Measurement | Genset1 | Alarms | Word13 | Genset1.Alarms.Word13 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39438 | Measurement | Genset1 | Alarms | Word14 | Genset1.Alarms.Word14 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 39439 | Measurement | Genset1 | Alarms | Word15 | Genset1.Alarms.Word15 |  | ushort | [6 empty] | FALSE | 3
[5 empty] | 772 | Measurement | Genset1 | Generator | OperatingMode | Genset1.Generator.OperatingMode | ushort | [7 empty] | TRUE | 3
[5 empty] | 768 | Parameter | Genset1 | Panel | ManufacturerCode | Genset1.Panel.ManufacturerCode | ushort | [7 empty] | FALSE | 3
[5 empty] | 769 | Parameter | Genset1 | Panel | ModelNumber | Genset1.Panel.ModelNumber | ushort | [7 empty] | FALSE | 3
[5 empty] | 770 | Parameter | Genset1 | Panel | SerialNumber | Genset1.Panel.SerialNumber | uint | [7 empty] | FALSE | 3
[5 empty] | 35200 | Parameter | Genset1 | Generator | ManualFrequencyTrim | Genset1.Generator.ManualFrequencyTrim | ushort | [7 empty] | FALSE | 3
[5 empty] | 35201 | Parameter | Genset1 | Generator | MinimumFrequencyTrim | Genset1.Generator.MinimumFrequencyTrim | ushort | [7 empty] | FALSE | 3
[5 empty] | 35202 | Parameter | Genset1 | Generator | MaximumFrequencyTrim | Genset1.Generator.MaximumFrequencyTrim | ushort | [7 empty] | FALSE | 3
[5 empty] | 2816 | Parameter | Genset1 | Panel | SoftwareVersion | Genset1.Panel.SoftwareVersion | ushort | [7 empty] | FALSE | 3